## AMD
XXXXX - Project Name | [17 empty] | XXXXX - Project Name | [22 empty] | XXXXX - Project Name
Estimated Maximum Electrical Demand | [17 empty] | Estimated Maximum Electrical Demand | [22 empty] | Estimated Maximum Electrical Demand
Manual Assessment | [17 empty] | Occupancy Profiles | [22 empty] | Occupancy Weighted Load Assessment
Blank/white cell = input required
| Grey cell = automated / filled cell | [10 empty] | Residential Section: (if applicable)
Type | Floor Area (m2) | Power Density |  |  | Discrete Load |  | Total Power (kW) | Design Demand |  | Apparent Power |  | Heat Demand (kW) |  |  | HWS | Instantaneous | [24 empty] | Type | Apparent Power (kVA) | Occupancy Profile | Apparent Power, Occupancy Weighted (kVA)
|  | Lighting (W/m2) | Small Power (W/m2) | HVAC (W/m2) | Quantity | Rated Load (kW) |  | Diversity | Design Demand (kW) | Power Factor | Apparent Power (kVA) | Source Type | Heat Pump | [6 empty] | Profile 1: | Morning/Evening
[12 empty] | COP (Heat Pump Only) | 3.5 | [6 empty] | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | AVG
[12 empty] | Electric Input (kW) | 0 | [5 empty] | Diversity | 0 | 0.5 | 0.7 | 0.7 | 0.5 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0.4 | 0.4 | 0.7 | 0.7 | 0.7 | 0.7 | 0.3 | 0.1 | 0 | 0.335 |  |  |  | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00
Discrete Loads | [40 empty] | Discrete Loads
[7 empty] | 0 | 1 | 0 | 0.95 | 0 | Apartment loadings | kW | P.F. | kVA | Diversity | kVA | [24 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 1 | 0 | 0.95 | 0 | Electric Heat Demand | 0 | 0.85 | 0 | 100% of 10 A + 50% | 0 | [24 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 1 | 0 | 0.95 | 0 | Hot Water Load | 3 | 0.95 | 3.1579 | 0 | 0 | [24 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 1 | 0 | 0.85 | 0 | Electric Oven | 2.4 | 0.95 | 2.5263 | 10A + 30% | 4.6732 | [24 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 1 | 0 | 0.95 | 0 | Electric Hob | 7.3 | 0.95 | 7.6842 |  |  |  |  | Profile 2: | Daytime | [20 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 1 | 0 | 0.95 | 0 | Fridge | 0.1 | 0.85 | 0.11765 | 0.3 | 0.035294 |  |  | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | AVG |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 1 | 0 | 0.95 | 0 | Dishwasher | 1 | 0.85 | 1.1765 | 0.3 | 0.35294 |  | Diversity | 0 | 0.3 | 0.6 | 0.7 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.7 | 0.6 | 0.3 | 0.1 | 0 | 0 | 0 | 0 | 0.515 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 1 | 0 | 0.95 | 0 | Washing machine | 2.2 | 0.85 | 2.5882 | 0.3 | 0.77647 | [24 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 1 | 0 | 0.95 | 0 | Sockets | 3 | 0.9 | 3.3333 | 0.3 | 1 | [24 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 1 | 0 | 0.95 | 0 | Lighting | 0.9 | 0.9 | 1 | 0.66 | 0.66 | [24 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 1 | 0 | 0.95 | 0 | TOTAL |  |  |  |  | 7.4979 | [24 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Room Density Loads | [40 empty] | Room Loads
[7 empty] | 0 | 1 | 0 | 0.95 | 0 | Building Diversity | Coincidence Factor | kVA Per flat | [5 empty] | Profile 3: | Evening Only | [20 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 1 | 0 | 0.95 | 0 | < 50 apartments | 0.7 | 5.2485 | [5 empty] | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | AVG |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 1 | 0 | 0.95 | 0 | 50-100 apartments | 0.6 | 4.4987 |  |  |  |  | Diversity | 0.9 | 0.7 | 0.4 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.4 | 0.7 | 0.8 | 0.95 | 0.95 | 0.95 | 0.95 | 0.405 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 1 | 0 | 0.95 | 0 | 100-200 apartments | 0.5 | 3.7489 | [27 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 1 | 0 | 0.95 | 0 | [30 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 1 | 0 | 0.95 | 0 | [30 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 1 | 0 | 0.95 | 0 | [30 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 1 | 0 | 0.95 | 0 | [30 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 1 | 0 | 0.95 | 0 | [8 empty] | Profile 4: | Occasional Use | [20 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 1 | 0 | 0.95 | 0 | [8 empty] | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | AVG |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 1 | 0 | 0.95 | 0 | [7 empty] | Diversity | 0 | 0.1 | 0.1 | 0.5 | 0.7 | 0.5 | 0.1 | 0.5 | 0.7 | 0.5 | 0.1 | 0.5 | 0.7 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0.28 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heating Load | [5 empty] | 0 | 0 | 1 | 0 | 0.95 | 0 | [29 empty] | Heating Load | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | January
Cooling Load | [5 empty] | 0 | 0 | 1 | 0 | 0.95 | 0 | [29 empty] | Cooling Load | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Life Safety Loads | [7 empty] | 0.4 |  |  | 0 | [29 empty] | Life Safety Loads | 0 | Profile 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Residential Loads | [40 empty] | Residential Loads
Residential Units from Table | [5 empty] | 0 |  | 0.7 |  |  | 0 | [29 empty] | Residential Units from Table | 0 | Dedicated Profile | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 1 | 0 | 0.95 | 0 | [8 empty] | Profile 5: | Afternoon | [20 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 1 | 0 | 0.95 | 0 | [8 empty] | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | AVG |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 1 | 0 | 0.95 | 0 | [7 empty] | Diversity | 0.2 | 0.3 | 0.4 | 0.3 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0.4 | 0.7 | 0.7 | 0.7 | 0.7 | 0.3 | 0.1 | 0 | 0.27 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 1 | 0 | 0.95 | 0 | [30 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[64 empty] | Avg Total (kVA) | 0
[5 empty] | Life Safety Loads: | [58 empty] | Avg Total (A) | 0
Total (kVA) | 0 |  |  |  | Loads |  | kW | Quantity | P.F. | Diversity | kVA | [29 empty] | Undiversified Total (kVA) | 0 | Diversified Total (kVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Max Total (kVA) | 0 | 0
Total (A) | 0 | [7 empty] | 0.85 | 1 | 0 | [29 empty] | Undiversified Total (A) | 0 | Diversified Total (A) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Max Total (A) | 0
[9 empty] | 0.85 | 1 | 0 | [8 empty] | Profile 6: | Flat Rate | 0.2
Rated Voltage (V) i.e. 3/1ø | 400 | [7 empty] | 0.85 | 1 | 0 | [8 empty] | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | AVG | Rated Voltage (V) i.e. 3/1ø | 400
[9 empty] | 0.85 | 1 | 0 | [7 empty] | Diversity | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Spare Capacity | 20% | [7 empty] | 0.85 | 1 | 0
Total + Spare (kVA) | 0 |  |  |  | TOTAL | [5 empty] | 0
Total + Spare (A) | 0
[7 empty] | © Henry Metcalfe, 2024 | [20 empty] | © Henry Metcalfe, 2024 | [20 empty] | © Henry Metcalfe, 2024
[16 empty] | 1 | Morning/Evening |  |  |  | Morning/Evening
[16 empty] | 2 | Daytime |  |  | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | AVG
[16 empty] | 3 | Evening Only |  | Diversity | 0 | 0.5 | 0.7 | 0.7 | 0.5 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0.4 | 0.4 | 0.7 | 0.7 | 0.7 | 0.7 | 0.3 | 0.1 | 0 | 0.335
[16 empty] | 4 | Occasional Use
[16 empty] | 5 | Hot Water Demand
[16 empty] | 6 | School/Education
[16 empty] | 7 | Restaurant
[16 empty] | 8 | Supermarket
[16 empty] | 9 | Student Accommodation |  |  |  | Daytime
[16 empty] | 10 | Afternoon |  |  | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | AVG
[19 empty] | Diversity | 0 | 0.3 | 0.6 | 0.7 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.7 | 0.6 | 0.3 | 0.1 | 0 | 0 | 0 | 0 | 0.515
Evening Only
[20 empty] | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | AVG
[19 empty] | Diversity | 0.9 | 0.7 | 0.4 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.4 | 0.7 | 0.8 | 0.95 | 0.95 | 0.95 | 0.95 | 0.405
Occasional Use
[20 empty] | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | AVG
[19 empty] | Diversity | 0 | 0.1 | 0.1 | 0.5 | 0.7 | 0.5 | 0.1 | 0.5 | 0.7 | 0.5 | 0.1 | 0.5 | 0.7 | 0.5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0.28
[21 empty] | Hot Water Demand |  |  | As per HWA/DG1 2018
[20 empty] | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | AVG
[19 empty] | Diversity | 0.1 | 0.25 | 0.73 | 0.77 | 0.65 | 0.53 | 0.47 | 0.43 | 0.42 | 0.4 | 0.36 | 0.32 | 0.37 | 0.49 | 0.56 | 0.73 | 0.77 | 0.73 | 0.4 | 0.2 | 0.484
[21 empty] | Flat Rate | 0.2
[20 empty] | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | AVG
[19 empty] | Diversity | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
School/Education
[20 empty] | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | AVG
[19 empty] | Diversity | 0.2 | 0.3 | 0.4 | 0.6 | 0.7 | 1 | 0.8 | 0.7 | 0.7 | 0.6 | 0.8 | 0.6 | 0.5 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.48
Restaurant
[20 empty] | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | AVG
[19 empty] | Diversity | 0.1 | 0.2 | 0.2 | 0.2 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | 1 | 0.6 | 0.6 | 0.8 | 1 | 1 | 0.8 | 0.6 | 0.4 | 0.2 | 0.1 | 0.59
Supermarket
[20 empty] | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | AVG
[19 empty] | Diversity | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.7 | 0.7 | 0.4 | 0.4 | 0.4 | 0.4 | 0.54
Student Accommodation
[20 empty] | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | AVG
[19 empty] | Diversity | 0 | 0 | 0 | 0.1 | 0.7 | 0.4 | 0.1 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.7 | 0.5 | 0.5 | 0.4 | 0.345
Afternoon
[20 empty] | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | AVG
[19 empty] | Diversity | 0.2 | 0.3 | 0.4 | 0.3 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0.4 | 0.7 | 0.7 | 0.7 | 0.7 | 0.3 | 0.1 | 0 | 0.27
Student Accommodation V2
[20 empty] | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | AVG
[19 empty] | Diversity | 0.353 | 0.372 | 0.415 | 0.458 | 0.485 | 0.487 | 0.502 | 0.521 | 0.531 | 0.52 | 0.511 | 0.526 | 0.576 | 0.672 | 0.722 | 0.701 | 0.673 | 0.634 | 0.588 | 0.518 | 0.53825
Note on R14: Henry Metcalfe: Danish Standard DS439
Note on A35: Henry Metcalfe: Refer to Degree Days Tab
Note on A36: Henry Metcalfe: Refer to Degree Days Tab
Note on I39: Henry Metcalfe: Information only, not calculated twice.

## DD
Max Heat Load |  | kW
COP | 3.5 |  | If electric panels, COP of 1 | [13 empty] | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | MAX
Max Electrical Heating Load | 0 | kW | [12 empty] | January | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Max Cooling Load |  | kW | [12 empty] | February | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
COP | 3.5 | [13 empty] | March | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Max Electrical Cooling Load | 0 | kW | [12 empty] | April | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[15 empty] | May | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Location | London Gatwick | [13 empty] | June | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Max HDD | 168 | [13 empty] | July | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Month of Max Heating | Jan | [13 empty] | August | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Max CDD | 19 | [13 empty] | September | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Month of Max Cooling | Jul | [13 empty] | October | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[15 empty] | November | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
London Gatwick | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total |  | December | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HDD base 10°C | 168 | 156 | 112 | 62 | 13 | 1 | 0 | 0 | 1 | 25 | 94 | 149 | 781 |  | January | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CDD base 18.3°C | 0 | 0 | 0 | 0 | 1 | 5 | 19 | 17 | 2 | 0 | 0 | 0 | 44 |  | February | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[15 empty] | March | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  |  | April | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heating Load (kW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | May | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Electrical Heating Load (kW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | June | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cooling Load (kW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | July | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Electrical Cooling Load (kW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | August | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[15 empty] | September | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[15 empty] | October | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
London Gatwick | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total |  | November | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HDD base 10°C | 168 | 156 | 112 | 62 | 13 | 1 | 0 | 0 | 1 | 25 | 94 | 149 | 781 |  | December | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CDD base 18.3°C | 0 | 0 | 0 | 0 | 1 | 5 | 19 | 17 | 2 | 0 | 0 | 0 | 44
[15 empty] | January | H&C | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Aberdeen Dyce | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total |  | February | H&C | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HDD base 10°C | 199 | 174 | 151 | 102 | 43 | 9 | 0 | 1 | 8 | 48 | 122 | 186 | 1043 |  | March | H&C | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CDD base 18.3°C | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 2 |  | April | H&C | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[15 empty] | May | H&C | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Aughton | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total |  | June | H&C | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HDD base 10°C | 174 | 163 | 124 | 74 | 18 | 2 | 0 | 0 | 2 | 26 | 94 | 145 | 822 |  | July | H&C | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CDD base 18.3°C | 0 | 0 | 0 | 0 | 0 | 3 | 8 | 7 | 1 | 0 | 0 | 0 | 19 |  | August | H&C | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[15 empty] | September | H&C | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Belfast | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total |  | October | H&C | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HDD base 10°C | 170 | 151 | 123 | 76 | 23 | 2 | 0 | 0 | 4 | 35 | 100 | 151 | 835 |  | November | H&C | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CDD base 18.3°C | 0 | 0 | 0 | 0 | 0 | 1 | 4 | 3 | 0 | 0 | 0 | 0 | 8 |  | December | H&C | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Birmingham | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
HDD base 10°C | 184 | 165 | 122 | 73 | 18 | 2 | 0 | 0 | 2 | 32 | 106 | 166 | 870
CDD base 18.3°C | 0 | 0 | 0 | 0 | 0 | 4 | 14 | 12 | 1 | 0 | 0 | 0 | 31
Finningley | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
HDD base 10°C | 192 | 175 | 126 | 78 | 21 | 3 | 0 | 0 | 3 | 36 | 111 | 158 | 903
CDD base 18.3°C | 0 | 0 | 0 | 0 | 0 | 3 | 12 | 11 | 1 | 0 | 0 | 0 | 27
Hemsby | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
HDD base 10°C | 172 | 158 | 122 | 73 | 18 | 1 | 0 | 0 | 1 | 18 | 87 | 143 | 793
CDD base 18.3°C | 0 | 0 | 0 | 0 | 0 | 2 | 7 | 10 | 1 | 0 | 0 | 0 | 20
Jersey | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
HDD base 10°C | 116 | 113 | 77 | 41 | 6 | 0 | 0 | 0 | 0 | 4 | 39 | 88 | 484
CDD base 18.3°C | 0 | 0 | 0 | 0 | 1 | 4 | 13 | 14 | 4 | 0 | 0 | 0 | 36
Leuchars | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
HDD base 10°C | 197 | 166 | 142 | 94 | 37 | 5 | 0 | 0 | 6 | 43 | 118 | 181 | 989
CDD base 18.3°C | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 1 | 0 | 0 | 0 | 5
Oban | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
HDD base 10°C | 158 | 139 | 122 | 74 | 17 | 2 | 0 | 0 | 4 | 31 | 88 | 141 | 776
CDD base 18.3°C | 0 | 0 | 0 | 0 | 1 | 2 | 3 | 4 | 0 | 0 | 0 | 0 | 10
Custom Location | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
HDD base 10°C | Total: 0
CDD base 18.3°C | Total: 0
| Apr: © Henry Metcalfe, 2024 | © Henry Metcalfe, 2024 | [10 empty] | © Henry Metcalfe, 2024

## Danish Standard DS439 (hidden)
Danish Standard DS 439
Number of Dwellings | Coincidence Factor
1 | 0.768
2 | 0.53781
3 | 0.43664
4 | 0.37662
5 | 0.33581
6 | 0.30577
7 | 0.28248
8 | 0.26374
9 | 0.24825
10 | 0.23516
11 | 0.22392
12 | 0.21412
13 | 0.20549
14 | 0.19781
15 | 0.19092
16 | 0.18469
17 | 0.17902
18 | 0.17384
19 | 0.16908
20 | 0.16468
21 | 0.1606
22 | 0.1568
23 | 0.15326
24 | 0.14995
25 | 0.14683
26 | 0.1439
27 | 0.14114
28 | 0.13852
29 | 0.13605
30 | 0.1337
31 | 0.13146
32 | 0.12933
33 | 0.1273
34 | 0.12537
35 | 0.12351
36 | 0.12174
37 | 0.12003
38 | 0.1184
39 | 0.11683
40 | 0.11532
41 | 0.11387
42 | 0.11246
43 | 0.11111
44 | 0.10981
45 | 0.10855
46 | 0.10733
47 | 0.10615
48 | 0.105
49 | 0.1039
50 | 0.10282
51 | 0.10178
52 | 0.10077
53 | 0.099789
54 | 0.098835
55 | 0.097907
56 | 0.097005
57 | 0.096126
58 | 0.095271
59 | 0.094437
60 | 0.093625
61 | 0.092833
62 | 0.09206
63 | 0.091306
64 | 0.09057
65 | 0.089851
66 | 0.089149
67 | 0.088462
68 | 0.087791
69 | 0.087135
70 | 0.086493
71 | 0.085865
72 | 0.08525
73 | 0.084647
74 | 0.084057
75 | 0.083479
76 | 0.082913
77 | 0.082358
78 | 0.081813
79 | 0.081279
80 | 0.080756
81 | 0.080242
82 | 0.079737
83 | 0.079242
84 | 0.078756
85 | 0.078278
86 | 0.077809
87 | 0.077348
88 | 0.076895
89 | 0.07645
90 | 0.076012
91 | 0.075581
92 | 0.075158
93 | 0.074741
94 | 0.074332
95 | 0.073928
96 | 0.073532
97 | 0.073141
98 | 0.072756
99 | 0.072378
100 | 0.072005
101 | 0.071637
102 | 0.071276
103 | 0.070919
104 | 0.070568
105 | 0.070221
106 | 0.06988
107 | 0.069544
108 | 0.069212
109 | 0.068885
110 | 0.068562
111 | 0.068244
112 | 0.06793
113 | 0.067621
114 | 0.067315
115 | 0.067014
116 | 0.066716
117 | 0.066422
118 | 0.066132
119 | 0.065846
120 | 0.065563
121 | 0.065284
122 | 0.065009
123 | 0.064737
124 | 0.064468
125 | 0.064202
126 | 0.06394
127 | 0.06368
128 | 0.063424
129 | 0.063171
130 | 0.062921
131 | 0.062673
132 | 0.062429
133 | 0.062187
134 | 0.061948
135 | 0.061712
136 | 0.061478
137 | 0.061247
138 | 0.061019
139 | 0.060793
140 | 0.060569
141 | 0.060348
142 | 0.060129
143 | 0.059913
144 | 0.059698
145 | 0.059486
146 | 0.059277
147 | 0.059069
148 | 0.058864
149 | 0.05866
150 | 0.058459
151 | 0.05826
152 | 0.058062
153 | 0.057867
154 | 0.057673
155 | 0.057482
156 | 0.057292
157 | 0.057104
158 | 0.056918
159 | 0.056734
160 | 0.056551
161 | 0.056371
162 | 0.056191
163 | 0.056014
164 | 0.055838
165 | 0.055664
166 | 0.055491
167 | 0.05532
168 | 0.055151
169 | 0.054983
170 | 0.054816
171 | 0.054651
172 | 0.054488
173 | 0.054326
174 | 0.054165
175 | 0.054006
176 | 0.053848
177 | 0.053691
178 | 0.053536
179 | 0.053382
180 | 0.053229
181 | 0.053078
182 | 0.052928
183 | 0.052779
184 | 0.052631
185 | 0.052485
186 | 0.05234
187 | 0.052196
188 | 0.052053
189 | 0.051911
190 | 0.05177
191 | 0.051631
192 | 0.051493
193 | 0.051355
194 | 0.051219
195 | 0.051084
196 | 0.05095
197 | 0.050817
198 | 0.050685
199 | 0.050553
200 | 0.050423

## PV
[29 empty] | Year | Month | Day | Time | P (W) | Constant | % of
| Battery Storage? | No | Shading Factor | % sky blocked by obstacles | Shading Factor | [9 empty] | Solar PV Data | [13 empty] | 2019 | January | 1 | 24 | 0 | 28500 | 0% | Sum of % of | Month
| Battery Peak Optimisation? | No | Heavy | >80% | 0.5 | [9 empty] | Latitude | 59 | [12 empty] | 2019 | January | 1 | 1 | 0 | 28500 | 0% | Time | January | February | March | April | May | June | July | August | September | October | November | December | Grand Total
| If yes, Battery Charge point (% max demand) | 30% | Significant | 60-80% | 0.65 | PV Panel Outputs and Sizes | [22 empty] | 2019 | January | 1 | 2 | 0 | 28500 | 0% | 1 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| If yes, Battery Discharge point (% max demand) | 80% | Modest | 20-60% | 0.8 | Manufacturer | Range | Model | Output (NMOT) (W) | Length | Width | Depth | W/m2 |  | Month | System Output | [12 empty] | 2019 | January | 1 | 3 | 0 | 28500 | 0% | 2 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| If yes, Battery Charge Rating (kWh) |  | None or Very Little | <20% | 1 | LG | Neon 2 | LG340N1C-V5 | 254 | 1686 | 1016 | 40 | 148.28 | 31 | Jan | 0 | [12 empty] | 2019 | January | 1 | 4 | 0 | 28500 | 0% | 3 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Solar PV: Capacity (kWp) |  |  |  |  | LG | Neon 2 | LG335N1C-V5 | 250 | 1686 | 1016 | 40 | 145.9448 | 28 | Feb | 0 | [12 empty] | 2019 | January | 1 | 5 | 0 | 28500 | 0% | 4 | 0% | 0% | 0% | 0% | 0% | 0.009521% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001027%
| Output per Panel (W) | 410 |  |  |  | LG | Neon 2 | LG365Q1C-A5 | 275 | 1686 | 1016 | 40 | 160.5393 | 31 | Mar | 0 | [12 empty] | 2019 | January | 1 | 6 | 0 | 28500 | 0% | 5 | 0% | 0% | 0% | 0.01277% | 0.3906% | 0.693% | 0.4615% | 0.07592% | 0% | 0% | 0% | 0% | 0.1883%
| Panel Width | 1.134 |  |  |  | LG | Neon R | LG360Q1C-A5 | 271 | 1686 | 1016 | 40 | 158.2042 | 30 | Apr | 0 | [12 empty] | 2019 | January | 1 | 7 | 0 | 28500 | 0% | 6 | 0% | 0% | 0.01201% | 0.7687% | 1.68% | 1.878% | 1.537% | 1.041% | 0.3582% | 0% | 0% | 0% | 0.8391%
| Panel Height | 1.722 |  |  |  | LG | Neon R | LG355Q1C-A5 | 267 | 1700 | 1016 | 40 | 154.5855 | 31 | May | 0 | [12 empty] | 2019 | January | 1 | 8 | 0 | 28500 | 0% | 7 | 0% | 0% | 2.188% | 3.84% | 4.817% | 4.945% | 4.455% | 3.998% | 3.548% | 2.278% | 0% | 0% | 3.216%
| No. Panels | 0 |  |  |  | LG | Neon R | LG350Q1C-A5 | 264 | 1700 | 1016 | 40 | 152.8485 | 30 | Jun | 0 | [12 empty] | 2019 | January | 1 | 9 | 983 | 28500 | 3.449% | 8 | 0.05394% | 4.577% | 6.717% | 7.057% | 7.887% | 8.011% | 7.481% | 7.397% | 7.972% | 8.291% | 3.783% | 0.0407% | 6.637%
| Array width in panels | 10 |  |  |  | Canadian Solar | Dymond - High Efficiency | CS6X-340P-FG | 251 | 1968 | 992 | 58 | 128.5692 | 31 | Jul | 0 | [12 empty] | 2019 | January | 1 | 10 | 7230.5 | 28500 | 25.37% | 9 | 7.896% | 9.994% | 10.44% | 9.991% | 10.56% | 9.978% | 10.13% | 9.762% | 10.62% | 12.53% | 10.53% | 8.903% | 10.18%
| Array height in panels | 0 |  |  |  | Canadian Solar | Dymond - High Efficiency | CS6X-345P-FG | 254 | 1968 | 992 | 58 | 130.1059 | 31 | Aug | 0 | [12 empty] | 2019 | January | 1 | 11 | 4909 | 28500 | 17.22% | 10 | 14.02% | 14.25% | 12.19% | 11.38% | 11.58% | 11.14% | 10.8% | 10.92% | 13.18% | 14.72% | 17.82% | 15.28% | 12.38%
| Array width (m) | 11.34 |  |  |  | Canadian Solar | Dymond - High Efficiency | CS6X-350P-FG | 258 | 1968 | 992 | 58 | 132.1548 | 30 | Sep | 0 | [12 empty] | 2019 | January | 1 | 12 | 5342 | 28500 | 18.74% | 11 | 17.75% | 15.36% | 13.54% | 12.83% | 12.41% | 11.31% | 11.42% | 12.78% | 13.05% | 13.63% | 18.42% | 21.4% | 13.48%
| Array Height (m) | 0 |  |  |  | Canadian Solar | Dymond - High Efficiency | CS6X-355P-FG | 262 | 1968 | 992 | 58 | 134.2037 | 31 | Oct | 0 | [12 empty] | 2019 | January | 1 | 13 | 5019.5 | 28500 | 17.61% | 12 | 19.99% | 15.44% | 13.12% | 13.13% | 11.9% | 11.56% | 11.85% | 13.01% | 12.35% | 14.62% | 17.4% | 22.27% | 13.58%
| Total area | 0 |  |  |  | Canadian Solar | Standard | CS6K 285P | 210 | 1650 | 992 | 35 | 128.2991 | 30 | Nov | 0 | [12 empty] | 2019 | January | 1 | 14 | 1646.5 | 28500 | 5.777% | 13 | 17.88% | 14.46% | 13.52% | 12.56% | 11.31% | 11.28% | 10.8% | 11.4% | 12.96% | 13.6% | 14.62% | 15.74% | 12.65%
[6 empty] | Canadian Solar | Standard | CS6K 290P | 214 | 1650 | 992 | 35 | 130.7429 | 31 | Dec | 0 | [12 empty] | 2019 | January | 1 | 15 | 1729 | 28500 | 6.067% | 14 | 14.41% | 12.15% | 10.88% | 10.45% | 9.778% | 9.643% | 10.72% | 10.92% | 10.45% | 10.05% | 11.37% | 11.56% | 10.72%
| Shading Factor | 1 |  |  |  | Canadian Solar | Standard | CS6K 295P | 218 | 1650 | 992 | 35 | 133.1867 |  | TOTAL | 0 | [12 empty] | 2019 | January | 1 | 16 | 0 | 28500 | 0% | 15 | 7.963% | 9.515% | 9.393% | 9.008% | 8.231% | 8.565% | 8.698% | 8.807% | 8.729% | 8.013% | 6.066% | 4.812% | 8.468%
| Inclination (degrees) | 40 |  |  |  | Canadian Solar | Standard | CS6K 300P | 221 | 1650 | 992 | 35 | 135.0196 |  | Rh-inc(orient, p,m) | [13 empty] | 2019 | January | 1 | 17 | 0 | 28500 | 0% | 16 | 0.03677% | 4.232% | 6.118% | 6.042% | 5.864% | 6.028% | 6.504% | 6.161% | 5.198% | 2.236% | 0.00264% | 0% | 4.979%
| Location | South East England |  |  |  | Canadian Solar | Standard | CS6K 305P | 225 | 1650 | 992 | 35 | 137.4633 | [15 empty] | 2019 | January | 1 | 18 | 0 | 28500 | 0% | 17 | 0% | 0.01749% | 1.883% | 2.651% | 2.85% | 3.456% | 3.659% | 3.083% | 1.563% | 0.03176% | 0% | 0% | 2.136%
31 | Orientation | S |  |  |  | JA Solar | Monocrystaline | JAM54S-30-410-MR-BF | 410 | 1722 | 1134 | 30 | 209.9605 |  | Jan | 1.9419 | [12 empty] | 2019 | January | 1 | 19 | 0 | 28500 | 0% | 18 | 0% | 0% | 0% | 0.2889% | 0.6837% | 1.121% | 1.214% | 0.6241% | 0.02496% | 0% | 0% | 0% | 0.4538%
28 | Outputs: | [13 empty] | Feb | 1.6807 | [12 empty] | 2019 | January | 1 | 20 | 0 | 28500 | 0% | 19 | 0% | 0% | 0% | 0% | 0.06882% | 0.3835% | 0.2777% | 0.01739% | 0% | 0% | 0% | 0% | 0.08371%
31 | Jan | 0 | [12 empty] | Mar | 1.3896 | [12 empty] | 2019 | January | 1 | 21 | 0 | 28500 | 0% | 20 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
30 | Feb | 0 | [12 empty] | Apr | 1.1694 | [12 empty] | 2019 | January | 1 | 22 | 0 | 28500 | 0% | 21 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
31 | Mar | 0 | [12 empty] | May | 1.0519 | [12 empty] | 2019 | January | 1 | 23 | 0 | 28500 | 0% | 22 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
30 | Apr | 0 | [12 empty] | Jun | 1.0096 | [12 empty] | 2019 | January | 2 | 24 | 0 | 28500 | 0% | 23 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
31 | May | 0 | [12 empty] | Jul | 1.0273 | [12 empty] | 2019 | January | 2 | 1 | 0 | 28500 | 0% | 24 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
31 | Jun | 0 | [12 empty] | Aug | 1.1133 | [12 empty] | 2019 | January | 2 | 2 | 0 | 28500 | 0% | Grand Total | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
30 | Jul | 0 | [12 empty] | Sep | 1.2902 | [12 empty] | 2019 | January | 2 | 3 | 0 | 28500 | 0%
31 | Aug | 0 | [12 empty] | Oct | 1.5624 | [12 empty] | 2019 | January | 2 | 4 | 0 | 28500 | 0%
30 | Sep | 0 | [12 empty] | Nov | 1.8614 | [12 empty] | 2019 | January | 2 | 5 | 0 | 28500 | 0%
31 | Oct | 0 | [12 empty] | Dec | 2.0261 | [12 empty] | 2019 | January | 2 | 6 | 0 | 28500 | 0%
| Nov | 0 | [26 empty] | 2019 | January | 2 | 7 | 0 | 28500 | 0%
| Dec | 0 | [13 empty] | Sh,m | [12 empty] | 2019 | January | 2 | 8 | 0 | 28500 | 0%
| TOTAL | 0 | [12 empty] | Jan | 32 | [12 empty] | 2019 | January | 2 | 9 | 5161 | 28500 | 18.11%
[15 empty] | Feb | 59 | [12 empty] | 2019 | January | 2 | 10 | 4476 | 28500 | 15.71%
[15 empty] | Mar | 104 | [12 empty] | 2019 | January | 2 | 11 | 8184.5 | 28500 | 28.72%
[15 empty] | Apr | 170 | [12 empty] | 2019 | January | 2 | 12 | 12206 | 28500 | 42.83%
[15 empty] | May | 208 | [12 empty] | 2019 | January | 2 | 13 | 4435.5 | 28500 | 15.56%
[15 empty] | Jun | 231 | [12 empty] | 2019 | January | 2 | 14 | 4159 | 28500 | 14.59%
[15 empty] | Jul | 216 | [12 empty] | 2019 | January | 2 | 15 | 1784 | 28500 | 6.26%
[15 empty] | Aug | 182 | [12 empty] | 2019 | January | 2 | 16 | 0 | 28500 | 0%
[15 empty] | Sep | 133 | [12 empty] | 2019 | January | 2 | 17 | 0 | 28500 | 0%
[15 empty] | Oct | 77 | [12 empty] | 2019 | January | 2 | 18 | 0 | 28500 | 0%
[15 empty] | Nov | 41 | [12 empty] | 2019 | January | 2 | 19 | 0 | 28500 | 0%
[15 empty] | Dec | 25 | [12 empty] | 2019 | January | 2 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 2 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 2 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 2 | 23 | 0 | 28500 | 0%
|  | © Henry Metcalfe, 2024 | [26 empty] | 2019 | January | 3 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 3 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 3 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 3 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 3 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 3 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 3 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 3 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 3 | 8 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 3 | 9 | 1401.5 | 28500 | 4.918%
[29 empty] | 2019 | January | 3 | 10 | 4214.5 | 28500 | 14.79%
[29 empty] | 2019 | January | 3 | 11 | 3855 | 28500 | 13.53%
[29 empty] | 2019 | January | 3 | 12 | 3775 | 28500 | 13.25%
[29 empty] | 2019 | January | 3 | 13 | 2732.5 | 28500 | 9.588%
[29 empty] | 2019 | January | 3 | 14 | 892.5 | 28500 | 3.132%
[14 empty] | k1 | -0.66 | [13 empty] | 2019 | January | 3 | 15 | 313 | 28500 | 1.098%
[14 empty] | k2 | -0.106 | [13 empty] | 2019 | January | 3 | 16 | 0 | 28500 | 0%
[14 empty] | k3 | 2.93 | [13 empty] | 2019 | January | 3 | 17 | 0 | 28500 | 0%
[14 empty] | k4 | 3.63 | [13 empty] | 2019 | January | 3 | 18 | 0 | 28500 | 0%
[14 empty] | k5 | -0.374 | [13 empty] | 2019 | January | 3 | 19 | 0 | 28500 | 0%
[14 empty] | k6 | -7.4 | [13 empty] | 2019 | January | 3 | 20 | 0 | 28500 | 0%
[14 empty] | k7 | -2.71 | 0.96331 | [12 empty] | 2019 | January | 3 | 21 | 0 | 28500 | 0%
[14 empty] | k8 | -0.991 | -2.4295 | [12 empty] | 2019 | January | 3 | 22 | 0 | 28500 | 0%
[14 empty] | k9 | 4.59 | 2.3455 | [12 empty] | 2019 | January | 3 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 4 | 24 | 0 | 28500 | 0%
[14 empty] | SAP 2012 version 9.92 (October 2013) | [14 empty] | 2019 | January | 4 | 1 | 0 | 28500 | 0%
[14 empty] | U3 | Solar radiation | [13 empty] | 2019 | January | 4 | 2 | 0 | 28500 | 0%
[14 empty] | U3.1 | Solar radiation on a horizontal plane | [13 empty] | 2019 | January | 4 | 3 | 0 | 28500 | 0%
[15 empty] | Table U3: Mean global solar irradiance (W/m2) on a horizontal plane, and solar declination | [13 empty] | 2019 | January | 4 | 4 | 0 | 28500 | 0%
[14 empty] | Region |  |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | 2019 | January | 4 | 5 | 0 | 28500 | 0%
[14 empty] | 0 | UK average | 0 UK average | 26 | 54 | 96 | 150 | 192 | 200 | 189 | 157 | 115 | 66 | 33 | 21 | 2019 | January | 4 | 6 | 0 | 28500 | 0%
[14 empty] | 1 | Thames | 1 Thames | 30 | 56 | 98 | 157 | 195 | 217 | 203 | 173 | 127 | 73 | 39 | 24 | 2019 | January | 4 | 7 | 0 | 28500 | 0%
[14 empty] | 2 | South East England | 2 South East England | 32 | 59 | 104 | 170 | 208 | 231 | 216 | 182 | 133 | 77 | 41 | 25 | 2019 | January | 4 | 8 | 0 | 28500 | 0%
[14 empty] | 3 | Southern England | 3 Southern England | 35 | 62 | 109 | 172 | 209 | 235 | 217 | 185 | 138 | 80 | 44 | 27 | 2019 | January | 4 | 9 | 11119.5 | 28500 | 39.02%
[14 empty] | 4 | South West England | 4 South West England | 36 | 63 | 111 | 174 | 210 | 233 | 204 | 182 | 136 | 78 | 44 | 28 | 2019 | January | 4 | 10 | 21972 | 28500 | 77.09%
[14 empty] | 5 | Severn Wales / Severn England | 5 Severn Wales / Severn England | 32 | 59 | 105 | 167 | 201 | 226 | 206 | 175 | 130 | 74 | 40 | 25 | 2019 | January | 4 | 11 | 28517 | 28500 | 100.1%
[14 empty] | 6 | Midlands | 6 Midlands | 28 | 55 | 97 | 153 | 191 | 208 | 194 | 163 | 121 | 69 | 35 | 23 | 2019 | January | 4 | 12 | 30326 | 28500 | 106.4%
[14 empty] | 7 | West Pennines Wales / West Pennines England | 7 West Pennines Wales / West Pennines England | 24 | 51 | 95 | 152 | 191 | 203 | 186 | 152 | 115 | 65 | 31 | 20 | 2019 | January | 4 | 13 | 31297 | 28500 | 109.8%
[14 empty] | 8 | North West England / South West Scotland | 8 North West England / South West Scotland | 23 | 51 | 95 | 157 | 200 | 203 | 194 | 156 | 113 | 62 | 30 | 19 | 2019 | January | 4 | 14 | 15802.5 | 28500 | 55.45%
[14 empty] | 9 | Borders Scotland / Borders England | 9 Borders Scotland / Borders England | 23 | 50 | 92 | 151 | 200 | 196 | 187 | 153 | 111 | 61 | 30 | 18 | 2019 | January | 4 | 15 | 8094 | 28500 | 28.4%
[14 empty] | 10 | North East England | 10 North East England | 25 | 51 | 95 | 152 | 196 | 198 | 190 | 156 | 115 | 64 | 32 | 20 | 2019 | January | 4 | 16 | 0 | 28500 | 0%
[14 empty] | 11 | East Pennines | 11 East Pennines | 26 | 54 | 96 | 150 | 192 | 200 | 189 | 157 | 115 | 66 | 33 | 21 | 2019 | January | 4 | 17 | 0 | 28500 | 0%
[14 empty] | 12 | East Anglia | 12 East Anglia | 30 | 58 | 101 | 165 | 203 | 220 | 206 | 173 | 128 | 74 | 39 | 24 | 2019 | January | 4 | 18 | 0 | 28500 | 0%
[14 empty] | 13 | Wales | 13 Wales | 29 | 57 | 104 | 164 | 205 | 220 | 199 | 167 | 120 | 68 | 35 | 22 | 2019 | January | 4 | 19 | 0 | 28500 | 0%
[14 empty] | 14 | West Scotland | 14 West Scotland | 19 | 46 | 88 | 148 | 196 | 193 | 185 | 150 | 101 | 55 | 25 | 15 | 2019 | January | 4 | 20 | 0 | 28500 | 0%
[14 empty] | 15 | East Scotland | 15 East Scotland | 21 | 46 | 89 | 146 | 198 | 191 | 183 | 150 | 106 | 57 | 27 | 15 | 2019 | January | 4 | 21 | 0 | 28500 | 0%
[14 empty] | 16 | North East Scotland | 16 North East Scotland | 19 | 45 | 89 | 143 | 194 | 188 | 177 | 144 | 101 | 54 | 25 | 14 | 2019 | January | 4 | 22 | 0 | 28500 | 0%
[14 empty] | 17 | Highland | 17 Highland | 17 | 43 | 85 | 145 | 189 | 185 | 170 | 139 | 98 | 51 | 22 | 12 | 2019 | January | 4 | 23 | 0 | 28500 | 0%
[14 empty] | 18 | Western Isles | 18 Western Isles | 16 | 41 | 87 | 155 | 205 | 206 | 185 | 148 | 101 | 51 | 21 | 11 | 2019 | January | 5 | 24 | 0 | 28500 | 0%
[14 empty] | 19 | Orkney | 19 Orkney | 14 | 39 | 84 | 143 | 205 | 201 | 178 | 145 | 100 | 50 | 19 | 9 | 2019 | January | 5 | 1 | 0 | 28500 | 0%
[14 empty] | 20 | Shetland | 20 Shetland | 12 | 34 | 79 | 135 | 196 | 190 | 168 | 144 | 90 | 46 | 16 | 7 | 2019 | January | 5 | 2 | 0 | 28500 | 0%
[14 empty] | 21 | Northern Ireland | 21 Northern Ireland | 24 | 52 | 96 | 155 | 201 | 198 | 183 | 150 | 107 | 61 | 30 | 18 | 2019 | January | 5 | 3 | 0 | 28500 | 0%
[17 empty] | Mar: Solar declination (°) | 2019 | January | 5 | 4 | 0 | 28500 | 0%
[14 empty] | All regions |  |  | -20.7 | -12.8 | -1.8 | 9.8 | 18.8 | 23.1 | 21.2 | 13.7 | 2.9 | -8.7 | -18.4 | -23 | 2019 | January | 5 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 5 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 5 | 7 | 0 | 28500 | 0%
[14 empty] | SAP 2012 version 9.92 (October 2013) | [14 empty] | 2019 | January | 5 | 8 | 0 | 28500 | 0%
[14 empty] | A = k 1 × sin3(p/2) + k2 × sin2(p/2) + k 3 × sin(p/2) | [14 empty] | 2019 | January | 5 | 9 | 289.5 | 28500 | 1.016%
[14 empty] | B = k 4 × sin3(p/2) + k 5 × sin2(p/2) + k6 × sin(p/2) |  |  | Feb: (U3) | 2019 | January | 5 | 10 | 1153 | 28500 | 4.046%
[14 empty] | C = k 7 × sin3(p/2) + k 8 × sin2(p/2) + k9 × sin(p/2) + 1 | [14 empty] | 2019 | January | 5 | 11 | 796.5 | 28500 | 2.795%
[14 empty] | The constants k1 to k9 depend on orientation as given in Table U5. | [14 empty] | 2019 | January | 5 | 12 | 1107 | 28500 | 3.884%
[14 empty] | For orientations other than those in Table U5, interpolate between two of the columns in the table for each of k1 to | [14 empty] | 2019 | January | 5 | 13 | 1140 | 28500 | 4%
[14 empty] | k9. For example for orientation 165° from North, interpolate between South-East (135°) and South (180°). | [14 empty] | 2019 | January | 5 | 14 | 656.5 | 28500 | 2.304%
[14 empty] | Table U5: Constants for calculation of solar flux on vertical and inclined surfaces | [14 empty] | 2019 | January | 5 | 15 | 313.5 | 28500 | 1.1%
[17 empty] | Jan: Orientation | 2019 | January | 5 | 16 | 0 | 28500 | 0%
[15 empty] | N | NE | NW | E | W | SE | SW | S | [6 empty] | 2019 | January | 5 | 17 | 0 | 28500 | 0%
[14 empty] | k1 | 26.3 | 0.165 | 0.165 | 1.44 | 1.44 | -2.95 | -2.95 | -0.66 | [6 empty] | 2019 | January | 5 | 18 | 0 | 28500 | 0%
[14 empty] | k2 | -38.5 | -3.68 | -3.68 | -2.36 | -2.36 | 2.89 | 2.89 | -0.106 | [6 empty] | 2019 | January | 5 | 19 | 0 | 28500 | 0%
[14 empty] | k3 | 14.8 | 3 | 3 | 1.07 | 1.07 | 1.17 | 1.17 | 2.93 | [6 empty] | 2019 | January | 5 | 20 | 0 | 28500 | 0%
[14 empty] | k4 | -16.5 | 6.38 | 6.38 | -0.514 | -0.514 | 5.67 | 5.67 | 3.63 | [6 empty] | 2019 | January | 5 | 21 | 0 | 28500 | 0%
[14 empty] | k5 | 27.3 | -4.53 | -4.53 | 1.89 | 1.89 | -3.54 | -3.54 | -0.374 | [6 empty] | 2019 | January | 5 | 22 | 0 | 28500 | 0%
[14 empty] | k6 | -11.9 | -0.405 | -0.405 | -1.64 | -1.64 | -4.28 | -4.28 | -7.4 | [6 empty] | 2019 | January | 5 | 23 | 0 | 28500 | 0%
[14 empty] | k7 | - 1.06 | -4.38 | -4.38 | -0.542 | -0.542 | -2.72 | -2.72 | -2.71 | [6 empty] | 2019 | January | 6 | 24 | 0 | 28500 | 0%
[14 empty] | k8 | 0.0872 | 4.89 | 4.89 | -0.757 | -0.757 | -0.25 | -0.25 | -0.991 | [6 empty] | 2019 | January | 6 | 1 | 0 | 28500 | 0%
[14 empty] | k9 | -0.191 | -1.99 | -1.99 | 0.604 | 0.604 | 3.07 | 3.07 | 4.59 | [6 empty] | 2019 | January | 6 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 6 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 6 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 6 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 6 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 6 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 6 | 8 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 6 | 9 | 725.5 | 28500 | 2.546%
[29 empty] | 2019 | January | 6 | 10 | 9233 | 28500 | 32.4%
[29 empty] | 2019 | January | 6 | 11 | 5505 | 28500 | 19.32%
[29 empty] | 2019 | January | 6 | 12 | 2848.5 | 28500 | 9.995%
[29 empty] | 2019 | January | 6 | 13 | 3924.5 | 28500 | 13.77%
[29 empty] | 2019 | January | 6 | 14 | 6792.5 | 28500 | 23.83%
[29 empty] | 2019 | January | 6 | 15 | 1750 | 28500 | 6.14%
[29 empty] | 2019 | January | 6 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 6 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 6 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 6 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 6 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 6 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 6 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 6 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 7 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 7 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 7 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 7 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 7 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 7 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 7 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 7 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 7 | 8 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 7 | 9 | 686 | 28500 | 2.407%
[29 empty] | 2019 | January | 7 | 10 | 4100.5 | 28500 | 14.39%
[29 empty] | 2019 | January | 7 | 11 | 1446 | 28500 | 5.074%
[29 empty] | 2019 | January | 7 | 12 | 1331 | 28500 | 4.67%
[29 empty] | 2019 | January | 7 | 13 | 1046 | 28500 | 3.67%
[29 empty] | 2019 | January | 7 | 14 | 483 | 28500 | 1.695%
[29 empty] | 2019 | January | 7 | 15 | 303.5 | 28500 | 1.065%
[29 empty] | 2019 | January | 7 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 7 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 7 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 7 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 7 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 7 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 7 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 7 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 8 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 8 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 8 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 8 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 8 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 8 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 8 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 8 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 8 | 8 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 8 | 9 | 12277 | 28500 | 43.08%
[29 empty] | 2019 | January | 8 | 10 | 23775.5 | 28500 | 83.42%
[29 empty] | 2019 | January | 8 | 11 | 27861 | 28500 | 97.76%
[29 empty] | 2019 | January | 8 | 12 | 30658 | 28500 | 107.6%
[29 empty] | 2019 | January | 8 | 13 | 26342 | 28500 | 92.43%
[29 empty] | 2019 | January | 8 | 14 | 20208 | 28500 | 70.91%
[29 empty] | 2019 | January | 8 | 15 | 11196.5 | 28500 | 39.29%
[29 empty] | 2019 | January | 8 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 8 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 8 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 8 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 8 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 8 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 8 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 8 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 9 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 9 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 9 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 9 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 9 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 9 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 9 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 9 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 9 | 8 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 9 | 9 | 2418.5 | 28500 | 8.486%
[29 empty] | 2019 | January | 9 | 10 | 7597.5 | 28500 | 26.66%
[29 empty] | 2019 | January | 9 | 11 | 10830 | 28500 | 38%
[29 empty] | 2019 | January | 9 | 12 | 13338.5 | 28500 | 46.8%
[29 empty] | 2019 | January | 9 | 13 | 24271 | 28500 | 85.16%
[29 empty] | 2019 | January | 9 | 14 | 12912 | 28500 | 45.31%
[29 empty] | 2019 | January | 9 | 15 | 3746.5 | 28500 | 13.15%
[29 empty] | 2019 | January | 9 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 9 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 9 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 9 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 9 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 9 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 9 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 9 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 10 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 10 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 10 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 10 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 10 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 10 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 10 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 10 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 10 | 8 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 10 | 9 | 2087 | 28500 | 7.323%
[29 empty] | 2019 | January | 10 | 10 | 1155.5 | 28500 | 4.054%
[29 empty] | 2019 | January | 10 | 11 | 2512.5 | 28500 | 8.816%
[29 empty] | 2019 | January | 10 | 12 | 2501.5 | 28500 | 8.777%
[29 empty] | 2019 | January | 10 | 13 | 2731.5 | 28500 | 9.584%
[29 empty] | 2019 | January | 10 | 14 | 1322 | 28500 | 4.639%
[29 empty] | 2019 | January | 10 | 15 | 593 | 28500 | 2.081%
[29 empty] | 2019 | January | 10 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 10 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 10 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 10 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 10 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 10 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 10 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 10 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 11 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 11 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 11 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 11 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 11 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 11 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 11 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 11 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 11 | 8 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 11 | 9 | 4827 | 28500 | 16.94%
[29 empty] | 2019 | January | 11 | 10 | 4698.5 | 28500 | 16.49%
[29 empty] | 2019 | January | 11 | 11 | 7069.5 | 28500 | 24.81%
[29 empty] | 2019 | January | 11 | 12 | 16368.5 | 28500 | 57.43%
[29 empty] | 2019 | January | 11 | 13 | 11639 | 28500 | 40.84%
[29 empty] | 2019 | January | 11 | 14 | 9785.5 | 28500 | 34.34%
[29 empty] | 2019 | January | 11 | 15 | 337.5 | 28500 | 1.184%
[29 empty] | 2019 | January | 11 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 11 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 11 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 11 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 11 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 11 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 11 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 11 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 12 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 12 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 12 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 12 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 12 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 12 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 12 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 12 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 12 | 8 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 12 | 9 | 614 | 28500 | 2.154%
[29 empty] | 2019 | January | 12 | 10 | 1441 | 28500 | 5.056%
[29 empty] | 2019 | January | 12 | 11 | 2179 | 28500 | 7.646%
[29 empty] | 2019 | January | 12 | 12 | 1654 | 28500 | 5.804%
[29 empty] | 2019 | January | 12 | 13 | 2135.5 | 28500 | 7.493%
[29 empty] | 2019 | January | 12 | 14 | 2409 | 28500 | 8.453%
[29 empty] | 2019 | January | 12 | 15 | 1027.5 | 28500 | 3.605%
[29 empty] | 2019 | January | 12 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 12 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 12 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 12 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 12 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 12 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 12 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 12 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 13 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 13 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 13 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 13 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 13 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 13 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 13 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 13 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 13 | 8 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 13 | 9 | 609.5 | 28500 | 2.139%
[29 empty] | 2019 | January | 13 | 10 | 1045 | 28500 | 3.667%
[29 empty] | 2019 | January | 13 | 11 | 24019 | 28500 | 84.28%
[29 empty] | 2019 | January | 13 | 12 | 16720 | 28500 | 58.67%
[29 empty] | 2019 | January | 13 | 13 | 9997.5 | 28500 | 35.08%
[29 empty] | 2019 | January | 13 | 14 | 11892.5 | 28500 | 41.73%
[29 empty] | 2019 | January | 13 | 15 | 4325 | 28500 | 15.18%
[29 empty] | 2019 | January | 13 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 13 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 13 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 13 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 13 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 13 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 13 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 13 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 14 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 14 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 14 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 14 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 14 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 14 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 14 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 14 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 14 | 8 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 14 | 9 | 15668.5 | 28500 | 54.98%
[29 empty] | 2019 | January | 14 | 10 | 22869.5 | 28500 | 80.24%
[29 empty] | 2019 | January | 14 | 11 | 2304.5 | 28500 | 8.086%
[29 empty] | 2019 | January | 14 | 12 | 1552 | 28500 | 5.446%
[29 empty] | 2019 | January | 14 | 13 | 1226 | 28500 | 4.302%
[29 empty] | 2019 | January | 14 | 14 | 1808.5 | 28500 | 6.346%
[29 empty] | 2019 | January | 14 | 15 | 2287.5 | 28500 | 8.026%
[29 empty] | 2019 | January | 14 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 14 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 14 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 14 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 14 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 14 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 14 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 14 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 15 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 15 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 15 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 15 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 15 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 15 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 15 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 15 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 15 | 8 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 15 | 9 | 5110.5 | 28500 | 17.93%
[29 empty] | 2019 | January | 15 | 10 | 3079 | 28500 | 10.8%
[29 empty] | 2019 | January | 15 | 11 | 5163 | 28500 | 18.12%
[29 empty] | 2019 | January | 15 | 12 | 9122 | 28500 | 32.01%
[29 empty] | 2019 | January | 15 | 13 | 4767 | 28500 | 16.73%
[29 empty] | 2019 | January | 15 | 14 | 2077.5 | 28500 | 7.289%
[29 empty] | 2019 | January | 15 | 15 | 144 | 28500 | 0.5053%
[29 empty] | 2019 | January | 15 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 15 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 15 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 15 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 15 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 15 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 15 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 15 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 16 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 16 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 16 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 16 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 16 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 16 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 16 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 16 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 16 | 8 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 16 | 9 | 1783.5 | 28500 | 6.258%
[29 empty] | 2019 | January | 16 | 10 | 334.5 | 28500 | 1.174%
[29 empty] | 2019 | January | 16 | 11 | 2219 | 28500 | 7.786%
[29 empty] | 2019 | January | 16 | 12 | 1012.5 | 28500 | 3.553%
[29 empty] | 2019 | January | 16 | 13 | 840.5 | 28500 | 2.949%
[29 empty] | 2019 | January | 16 | 14 | 1149.5 | 28500 | 4.033%
[29 empty] | 2019 | January | 16 | 15 | 1144 | 28500 | 4.014%
[29 empty] | 2019 | January | 16 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 16 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 16 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 16 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 16 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 16 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 16 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 16 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 17 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 17 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 17 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 17 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 17 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 17 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 17 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 17 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 17 | 8 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 17 | 9 | 1726 | 28500 | 6.056%
[29 empty] | 2019 | January | 17 | 10 | 27815.5 | 28500 | 97.6%
[29 empty] | 2019 | January | 17 | 11 | 32509 | 28500 | 114.1%
[29 empty] | 2019 | January | 17 | 12 | 34905.5 | 28500 | 122.5%
[29 empty] | 2019 | January | 17 | 13 | 33206.5 | 28500 | 116.5%
[29 empty] | 2019 | January | 17 | 14 | 25869 | 28500 | 90.77%
[29 empty] | 2019 | January | 17 | 15 | 17851 | 28500 | 62.64%
[29 empty] | 2019 | January | 17 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 17 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 17 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 17 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 17 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 17 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 17 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 17 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 18 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 18 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 18 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 18 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 18 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 18 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 18 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 18 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 18 | 8 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 18 | 9 | 4603.5 | 28500 | 16.15%
[29 empty] | 2019 | January | 18 | 10 | 23873.5 | 28500 | 83.77%
[29 empty] | 2019 | January | 18 | 11 | 27623 | 28500 | 96.92%
[29 empty] | 2019 | January | 18 | 12 | 30037 | 28500 | 105.4%
[29 empty] | 2019 | January | 18 | 13 | 22149.5 | 28500 | 77.72%
[29 empty] | 2019 | January | 18 | 14 | 20435.5 | 28500 | 71.7%
[29 empty] | 2019 | January | 18 | 15 | 2940.5 | 28500 | 10.32%
[29 empty] | 2019 | January | 18 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 18 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 18 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 18 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 18 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 18 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 18 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 18 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 19 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 19 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 19 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 19 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 19 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 19 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 19 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 19 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 19 | 8 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 19 | 9 | 4093.5 | 28500 | 14.36%
[29 empty] | 2019 | January | 19 | 10 | 2052.5 | 28500 | 7.202%
[29 empty] | 2019 | January | 19 | 11 | 3420.5 | 28500 | 12%
[29 empty] | 2019 | January | 19 | 12 | 2353 | 28500 | 8.256%
[29 empty] | 2019 | January | 19 | 13 | 1472 | 28500 | 5.165%
[29 empty] | 2019 | January | 19 | 14 | 2465.5 | 28500 | 8.651%
[29 empty] | 2019 | January | 19 | 15 | 6839.5 | 28500 | 24%
[29 empty] | 2019 | January | 19 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 19 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 19 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 19 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 19 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 19 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 19 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 19 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 20 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 20 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 20 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 20 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 20 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 20 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 20 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 20 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 20 | 8 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 20 | 9 | 18528.5 | 28500 | 65.01%
[29 empty] | 2019 | January | 20 | 10 | 28105 | 28500 | 98.61%
[29 empty] | 2019 | January | 20 | 11 | 32541 | 28500 | 114.2%
[29 empty] | 2019 | January | 20 | 12 | 35012 | 28500 | 122.8%
[29 empty] | 2019 | January | 20 | 13 | 32997.5 | 28500 | 115.8%
[29 empty] | 2019 | January | 20 | 14 | 28005 | 28500 | 98.26%
[29 empty] | 2019 | January | 20 | 15 | 17949 | 28500 | 62.98%
[29 empty] | 2019 | January | 20 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 20 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 20 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 20 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 20 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 20 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 20 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 20 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 21 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 21 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 21 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 21 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 21 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 21 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 21 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 21 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 21 | 8 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 21 | 9 | 10398 | 28500 | 36.48%
[29 empty] | 2019 | January | 21 | 10 | 9172 | 28500 | 32.18%
[29 empty] | 2019 | January | 21 | 11 | 24233.5 | 28500 | 85.03%
[29 empty] | 2019 | January | 21 | 12 | 29716.5 | 28500 | 104.3%
[29 empty] | 2019 | January | 21 | 13 | 25818 | 28500 | 90.59%
[29 empty] | 2019 | January | 21 | 14 | 23190.5 | 28500 | 81.37%
[29 empty] | 2019 | January | 21 | 15 | 10210.5 | 28500 | 35.83%
[29 empty] | 2019 | January | 21 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 21 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 21 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 21 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 21 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 21 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 21 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 21 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 22 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 22 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 22 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 22 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 22 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 22 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 22 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 22 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 22 | 8 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 22 | 9 | 17187 | 28500 | 60.31%
[29 empty] | 2019 | January | 22 | 10 | 28572 | 28500 | 100.3%
[29 empty] | 2019 | January | 22 | 11 | 31439.5 | 28500 | 110.3%
[29 empty] | 2019 | January | 22 | 12 | 33534.5 | 28500 | 117.7%
[29 empty] | 2019 | January | 22 | 13 | 30982.5 | 28500 | 108.7%
[29 empty] | 2019 | January | 22 | 14 | 28335 | 28500 | 99.42%
[29 empty] | 2019 | January | 22 | 15 | 757 | 28500 | 2.656%
[29 empty] | 2019 | January | 22 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 22 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 22 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 22 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 22 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 22 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 22 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 22 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 23 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 23 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 23 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 23 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 23 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 23 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 23 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 23 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 23 | 8 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 23 | 9 | 1854 | 28500 | 6.505%
[29 empty] | 2019 | January | 23 | 10 | 6302.5 | 28500 | 22.11%
[29 empty] | 2019 | January | 23 | 11 | 1457 | 28500 | 5.112%
[29 empty] | 2019 | January | 23 | 12 | 2690.5 | 28500 | 9.44%
[29 empty] | 2019 | January | 23 | 13 | 2136 | 28500 | 7.495%
[29 empty] | 2019 | January | 23 | 14 | 1979 | 28500 | 6.944%
[29 empty] | 2019 | January | 23 | 15 | 2674.5 | 28500 | 9.384%
[29 empty] | 2019 | January | 23 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 23 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 23 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 23 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 23 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 23 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 23 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 23 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 24 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 24 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 24 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 24 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 24 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 24 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 24 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 24 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 24 | 8 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 24 | 9 | 2435 | 28500 | 8.544%
[29 empty] | 2019 | January | 24 | 10 | 2214.5 | 28500 | 7.77%
[29 empty] | 2019 | January | 24 | 11 | 2012.5 | 28500 | 7.061%
[29 empty] | 2019 | January | 24 | 12 | 2860.5 | 28500 | 10.04%
[29 empty] | 2019 | January | 24 | 13 | 1619.5 | 28500 | 5.682%
[29 empty] | 2019 | January | 24 | 14 | 2100.5 | 28500 | 7.37%
[29 empty] | 2019 | January | 24 | 15 | 9214.5 | 28500 | 32.33%
[29 empty] | 2019 | January | 24 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 24 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 24 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 24 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 24 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 24 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 24 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 24 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 25 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 25 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 25 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 25 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 25 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 25 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 25 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 25 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 25 | 8 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 25 | 9 | 17805.5 | 28500 | 62.48%
[29 empty] | 2019 | January | 25 | 10 | 2661 | 28500 | 9.337%
[29 empty] | 2019 | January | 25 | 11 | 5421.5 | 28500 | 19.02%
[29 empty] | 2019 | January | 25 | 12 | 9425 | 28500 | 33.07%
[29 empty] | 2019 | January | 25 | 13 | 8061 | 28500 | 28.28%
[29 empty] | 2019 | January | 25 | 14 | 5916 | 28500 | 20.76%
[29 empty] | 2019 | January | 25 | 15 | 1813.5 | 28500 | 6.363%
[29 empty] | 2019 | January | 25 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 25 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 25 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 25 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 25 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 25 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 25 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 25 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 26 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 26 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 26 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 26 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 26 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 26 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 26 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 26 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 26 | 8 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 26 | 9 | 1195 | 28500 | 4.193%
[29 empty] | 2019 | January | 26 | 10 | 6681.5 | 28500 | 23.44%
[29 empty] | 2019 | January | 26 | 11 | 9961 | 28500 | 34.95%
[29 empty] | 2019 | January | 26 | 12 | 7351 | 28500 | 25.79%
[29 empty] | 2019 | January | 26 | 13 | 10991 | 28500 | 38.56%
[29 empty] | 2019 | January | 26 | 14 | 1042 | 28500 | 3.656%
[29 empty] | 2019 | January | 26 | 15 | 1929 | 28500 | 6.768%
[29 empty] | 2019 | January | 26 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 26 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 26 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 26 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 26 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 26 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 26 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 26 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 27 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 27 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 27 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 27 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 27 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 27 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 27 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 27 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 27 | 8 | 15.5 | 28500 | 0.05439%
[29 empty] | 2019 | January | 27 | 9 | 7755 | 28500 | 27.21%
[29 empty] | 2019 | January | 27 | 10 | 26355.5 | 28500 | 92.48%
[29 empty] | 2019 | January | 27 | 11 | 6444 | 28500 | 22.61%
[29 empty] | 2019 | January | 27 | 12 | 1724.5 | 28500 | 6.051%
[29 empty] | 2019 | January | 27 | 13 | 1241.5 | 28500 | 4.356%
[29 empty] | 2019 | January | 27 | 14 | 689 | 28500 | 2.418%
[29 empty] | 2019 | January | 27 | 15 | 2828 | 28500 | 9.923%
[29 empty] | 2019 | January | 27 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 27 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 27 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 27 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 27 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 27 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 27 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 27 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 28 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 28 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 28 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 28 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 28 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 28 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 28 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 28 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 28 | 8 | 102.5 | 28500 | 0.3596%
[29 empty] | 2019 | January | 28 | 9 | 18466.5 | 28500 | 64.79%
[29 empty] | 2019 | January | 28 | 10 | 28462 | 28500 | 99.87%
[29 empty] | 2019 | January | 28 | 11 | 32330 | 28500 | 113.4%
[29 empty] | 2019 | January | 28 | 12 | 32462 | 28500 | 113.9%
[29 empty] | 2019 | January | 28 | 13 | 30881 | 28500 | 108.4%
[29 empty] | 2019 | January | 28 | 14 | 24170.5 | 28500 | 84.81%
[29 empty] | 2019 | January | 28 | 15 | 18008.5 | 28500 | 63.19%
[29 empty] | 2019 | January | 28 | 16 | 452.5 | 28500 | 1.588%
[29 empty] | 2019 | January | 28 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 28 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 28 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 28 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 28 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 28 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 28 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 29 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 29 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 29 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 29 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 29 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 29 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 29 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 29 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 29 | 8 | 127.5 | 28500 | 0.4474%
[29 empty] | 2019 | January | 29 | 9 | 11278 | 28500 | 39.57%
[29 empty] | 2019 | January | 29 | 10 | 17675 | 28500 | 62.02%
[29 empty] | 2019 | January | 29 | 11 | 29598.5 | 28500 | 103.9%
[29 empty] | 2019 | January | 29 | 12 | 18529 | 28500 | 65.01%
[29 empty] | 2019 | January | 29 | 13 | 12464.5 | 28500 | 43.74%
[29 empty] | 2019 | January | 29 | 14 | 6332 | 28500 | 22.22%
[29 empty] | 2019 | January | 29 | 15 | 7252.5 | 28500 | 25.45%
[29 empty] | 2019 | January | 29 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 29 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 29 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 29 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 29 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 29 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 29 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 29 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 30 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 30 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 30 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 30 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 30 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 30 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 30 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 30 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 30 | 8 | 735.5 | 28500 | 2.581%
[29 empty] | 2019 | January | 30 | 9 | 17361 | 28500 | 60.92%
[29 empty] | 2019 | January | 30 | 10 | 23725.5 | 28500 | 83.25%
[29 empty] | 2019 | January | 30 | 11 | 30221.5 | 28500 | 106%
[29 empty] | 2019 | January | 30 | 12 | 32360 | 28500 | 113.5%
[29 empty] | 2019 | January | 30 | 13 | 30768.5 | 28500 | 108%
[29 empty] | 2019 | January | 30 | 14 | 18472 | 28500 | 64.81%
[29 empty] | 2019 | January | 30 | 15 | 18959 | 28500 | 66.52%
[29 empty] | 2019 | January | 30 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 30 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 30 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 30 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 30 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 30 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 30 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 30 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 31 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 31 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 31 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 31 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 31 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 31 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 31 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 31 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 31 | 8 | 447 | 28500 | 1.568%
[29 empty] | 2019 | January | 31 | 9 | 13763 | 28500 | 48.29%
[29 empty] | 2019 | January | 31 | 10 | 23547 | 28500 | 82.62%
[29 empty] | 2019 | January | 31 | 11 | 29938 | 28500 | 105%
[29 empty] | 2019 | January | 31 | 12 | 5942.5 | 28500 | 20.85%
[29 empty] | 2019 | January | 31 | 13 | 18784 | 28500 | 65.91%
[29 empty] | 2019 | January | 31 | 14 | 10062 | 28500 | 35.31%
[29 empty] | 2019 | January | 31 | 15 | 5015 | 28500 | 17.6%
[29 empty] | 2019 | January | 31 | 16 | 101.5 | 28500 | 0.3561%
[29 empty] | 2019 | January | 31 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 31 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 31 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 31 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 31 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 31 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | January | 31 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 1 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 1 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 1 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 1 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 1 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 1 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 1 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 1 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 1 | 8 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 1 | 9 | 668 | 28500 | 2.344%
[29 empty] | 2019 | February | 1 | 10 | 975.5 | 28500 | 3.423%
[29 empty] | 2019 | February | 1 | 11 | 1479 | 28500 | 5.189%
[29 empty] | 2019 | February | 1 | 12 | 1664.5 | 28500 | 5.84%
[29 empty] | 2019 | February | 1 | 13 | 1775 | 28500 | 6.228%
[29 empty] | 2019 | February | 1 | 14 | 1041 | 28500 | 3.653%
[29 empty] | 2019 | February | 1 | 15 | 5940.5 | 28500 | 20.84%
[29 empty] | 2019 | February | 1 | 16 | 78 | 28500 | 0.2737%
[29 empty] | 2019 | February | 1 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 1 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 1 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 1 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 1 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 1 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 1 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 2 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 2 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 2 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 2 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 2 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 2 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 2 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 2 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 2 | 8 | 16.5 | 28500 | 0.05789%
[29 empty] | 2019 | February | 2 | 9 | 9316.5 | 28500 | 32.69%
[29 empty] | 2019 | February | 2 | 10 | 15146 | 28500 | 53.14%
[29 empty] | 2019 | February | 2 | 11 | 10568 | 28500 | 37.08%
[29 empty] | 2019 | February | 2 | 12 | 2907.5 | 28500 | 10.2%
[29 empty] | 2019 | February | 2 | 13 | 3065 | 28500 | 10.75%
[29 empty] | 2019 | February | 2 | 14 | 466.5 | 28500 | 1.637%
[29 empty] | 2019 | February | 2 | 15 | 5022 | 28500 | 17.62%
[29 empty] | 2019 | February | 2 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 2 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 2 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 2 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 2 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 2 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 2 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 2 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 3 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 3 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 3 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 3 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 3 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 3 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 3 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 3 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 3 | 8 | 1090 | 28500 | 3.825%
[29 empty] | 2019 | February | 3 | 9 | 19872 | 28500 | 69.73%
[29 empty] | 2019 | February | 3 | 10 | 27426 | 28500 | 96.23%
[29 empty] | 2019 | February | 3 | 11 | 34809.5 | 28500 | 122.1%
[29 empty] | 2019 | February | 3 | 12 | 33577.5 | 28500 | 117.8%
[29 empty] | 2019 | February | 3 | 13 | 33712.5 | 28500 | 118.3%
[29 empty] | 2019 | February | 3 | 14 | 26613.5 | 28500 | 93.38%
[29 empty] | 2019 | February | 3 | 15 | 21937 | 28500 | 76.97%
[29 empty] | 2019 | February | 3 | 16 | 603.5 | 28500 | 2.118%
[29 empty] | 2019 | February | 3 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 3 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 3 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 3 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 3 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 3 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 3 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 4 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 4 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 4 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 4 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 4 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 4 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 4 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 4 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 4 | 8 | 147.5 | 28500 | 0.5175%
[29 empty] | 2019 | February | 4 | 9 | 654 | 28500 | 2.295%
[29 empty] | 2019 | February | 4 | 10 | 2212 | 28500 | 7.761%
[29 empty] | 2019 | February | 4 | 11 | 1827 | 28500 | 6.411%
[29 empty] | 2019 | February | 4 | 12 | 4815 | 28500 | 16.89%
[29 empty] | 2019 | February | 4 | 13 | 1409.5 | 28500 | 4.946%
[29 empty] | 2019 | February | 4 | 14 | 4801 | 28500 | 16.85%
[29 empty] | 2019 | February | 4 | 15 | 7288.5 | 28500 | 25.57%
[29 empty] | 2019 | February | 4 | 16 | 195.5 | 28500 | 0.686%
[29 empty] | 2019 | February | 4 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 4 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 4 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 4 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 4 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 4 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 4 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 5 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 5 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 5 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 5 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 5 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 5 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 5 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 5 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 5 | 8 | 1117.5 | 28500 | 3.921%
[29 empty] | 2019 | February | 5 | 9 | 1670.5 | 28500 | 5.861%
[29 empty] | 2019 | February | 5 | 10 | 2844 | 28500 | 9.979%
[29 empty] | 2019 | February | 5 | 11 | 1958.5 | 28500 | 6.872%
[29 empty] | 2019 | February | 5 | 12 | 1878.5 | 28500 | 6.591%
[29 empty] | 2019 | February | 5 | 13 | 1582 | 28500 | 5.551%
[29 empty] | 2019 | February | 5 | 14 | 1476 | 28500 | 5.179%
[29 empty] | 2019 | February | 5 | 15 | 2481.5 | 28500 | 8.707%
[29 empty] | 2019 | February | 5 | 16 | 365.5 | 28500 | 1.282%
[29 empty] | 2019 | February | 5 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 5 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 5 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 5 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 5 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 5 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 5 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 6 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 6 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 6 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 6 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 6 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 6 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 6 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 6 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 6 | 8 | 3020.5 | 28500 | 10.6%
[29 empty] | 2019 | February | 6 | 9 | 12836 | 28500 | 45.04%
[29 empty] | 2019 | February | 6 | 10 | 17421 | 28500 | 61.13%
[29 empty] | 2019 | February | 6 | 11 | 11619.5 | 28500 | 40.77%
[29 empty] | 2019 | February | 6 | 12 | 8326 | 28500 | 29.21%
[29 empty] | 2019 | February | 6 | 13 | 12328.5 | 28500 | 43.26%
[29 empty] | 2019 | February | 6 | 14 | 6214.5 | 28500 | 21.81%
[29 empty] | 2019 | February | 6 | 15 | 10823 | 28500 | 37.98%
[29 empty] | 2019 | February | 6 | 16 | 936.5 | 28500 | 3.286%
[29 empty] | 2019 | February | 6 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 6 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 6 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 6 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 6 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 6 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 6 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 7 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 7 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 7 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 7 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 7 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 7 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 7 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 7 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 7 | 8 | 7936.5 | 28500 | 27.85%
[29 empty] | 2019 | February | 7 | 9 | 21486 | 28500 | 75.39%
[29 empty] | 2019 | February | 7 | 10 | 20874 | 28500 | 73.24%
[29 empty] | 2019 | February | 7 | 11 | 21746 | 28500 | 76.3%
[29 empty] | 2019 | February | 7 | 12 | 29230 | 28500 | 102.6%
[29 empty] | 2019 | February | 7 | 13 | 32561.5 | 28500 | 114.3%
[29 empty] | 2019 | February | 7 | 14 | 10110 | 28500 | 35.47%
[29 empty] | 2019 | February | 7 | 15 | 21993.5 | 28500 | 77.17%
[29 empty] | 2019 | February | 7 | 16 | 8377 | 28500 | 29.39%
[29 empty] | 2019 | February | 7 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 7 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 7 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 7 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 7 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 7 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 7 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 8 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 8 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 8 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 8 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 8 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 8 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 8 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 8 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 8 | 8 | 277 | 28500 | 0.9719%
[29 empty] | 2019 | February | 8 | 9 | 707.5 | 28500 | 2.482%
[29 empty] | 2019 | February | 8 | 10 | 1617.5 | 28500 | 5.675%
[29 empty] | 2019 | February | 8 | 11 | 2863 | 28500 | 10.05%
[29 empty] | 2019 | February | 8 | 12 | 4548.5 | 28500 | 15.96%
[29 empty] | 2019 | February | 8 | 13 | 3203.5 | 28500 | 11.24%
[29 empty] | 2019 | February | 8 | 14 | 4259.5 | 28500 | 14.95%
[29 empty] | 2019 | February | 8 | 15 | 3908 | 28500 | 13.71%
[29 empty] | 2019 | February | 8 | 16 | 95.5 | 28500 | 0.3351%
[29 empty] | 2019 | February | 8 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 8 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 8 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 8 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 8 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 8 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 8 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 9 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 9 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 9 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 9 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 9 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 9 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 9 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 9 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 9 | 8 | 8307 | 28500 | 29.15%
[29 empty] | 2019 | February | 9 | 9 | 15299 | 28500 | 53.68%
[29 empty] | 2019 | February | 9 | 10 | 24935 | 28500 | 87.49%
[29 empty] | 2019 | February | 9 | 11 | 34481 | 28500 | 121%
[29 empty] | 2019 | February | 9 | 12 | 37684.5 | 28500 | 132.2%
[29 empty] | 2019 | February | 9 | 13 | 23497 | 28500 | 82.45%
[29 empty] | 2019 | February | 9 | 14 | 21938.5 | 28500 | 76.98%
[29 empty] | 2019 | February | 9 | 15 | 7263.5 | 28500 | 25.49%
[29 empty] | 2019 | February | 9 | 16 | 2748.5 | 28500 | 9.644%
[29 empty] | 2019 | February | 9 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 9 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 9 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 9 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 9 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 9 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 9 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 10 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 10 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 10 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 10 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 10 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 10 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 10 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 10 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 10 | 8 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 10 | 9 | 4640.5 | 28500 | 16.28%
[29 empty] | 2019 | February | 10 | 10 | 2640 | 28500 | 9.263%
[29 empty] | 2019 | February | 10 | 11 | 4162.5 | 28500 | 14.61%
[29 empty] | 2019 | February | 10 | 12 | 3439.5 | 28500 | 12.07%
[29 empty] | 2019 | February | 10 | 13 | 7279.5 | 28500 | 25.54%
[29 empty] | 2019 | February | 10 | 14 | 9262 | 28500 | 32.5%
[29 empty] | 2019 | February | 10 | 15 | 11460 | 28500 | 40.21%
[29 empty] | 2019 | February | 10 | 16 | 429.5 | 28500 | 1.507%
[29 empty] | 2019 | February | 10 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 10 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 10 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 10 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 10 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 10 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 10 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 11 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 11 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 11 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 11 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 11 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 11 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 11 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 11 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 11 | 8 | 3368 | 28500 | 11.82%
[29 empty] | 2019 | February | 11 | 9 | 10043.5 | 28500 | 35.24%
[29 empty] | 2019 | February | 11 | 10 | 29517 | 28500 | 103.6%
[29 empty] | 2019 | February | 11 | 11 | 32818.5 | 28500 | 115.2%
[29 empty] | 2019 | February | 11 | 12 | 19994.5 | 28500 | 70.16%
[29 empty] | 2019 | February | 11 | 13 | 14059 | 28500 | 49.33%
[29 empty] | 2019 | February | 11 | 14 | 10003 | 28500 | 35.1%
[29 empty] | 2019 | February | 11 | 15 | 4257.5 | 28500 | 14.94%
[29 empty] | 2019 | February | 11 | 16 | 97 | 28500 | 0.3404%
[29 empty] | 2019 | February | 11 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 11 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 11 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 11 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 11 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 11 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 11 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 12 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 12 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 12 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 12 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 12 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 12 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 12 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 12 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 12 | 8 | 4879.5 | 28500 | 17.12%
[29 empty] | 2019 | February | 12 | 9 | 18567 | 28500 | 65.15%
[29 empty] | 2019 | February | 12 | 10 | 25721 | 28500 | 90.25%
[29 empty] | 2019 | February | 12 | 11 | 18347 | 28500 | 64.38%
[29 empty] | 2019 | February | 12 | 12 | 19408 | 28500 | 68.1%
[29 empty] | 2019 | February | 12 | 13 | 12748.5 | 28500 | 44.73%
[29 empty] | 2019 | February | 12 | 14 | 23032 | 28500 | 80.81%
[29 empty] | 2019 | February | 12 | 15 | 11093.5 | 28500 | 38.92%
[29 empty] | 2019 | February | 12 | 16 | 542.5 | 28500 | 1.904%
[29 empty] | 2019 | February | 12 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 12 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 12 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 12 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 12 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 12 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 12 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 13 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 13 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 13 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 13 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 13 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 13 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 13 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 13 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 13 | 8 | 1887.5 | 28500 | 6.623%
[29 empty] | 2019 | February | 13 | 9 | 6306 | 28500 | 22.13%
[29 empty] | 2019 | February | 13 | 10 | 8123.5 | 28500 | 28.5%
[29 empty] | 2019 | February | 13 | 11 | 17844.5 | 28500 | 62.61%
[29 empty] | 2019 | February | 13 | 12 | 22274 | 28500 | 78.15%
[29 empty] | 2019 | February | 13 | 13 | 23671.5 | 28500 | 83.06%
[29 empty] | 2019 | February | 13 | 14 | 28995.5 | 28500 | 101.7%
[29 empty] | 2019 | February | 13 | 15 | 17192 | 28500 | 60.32%
[29 empty] | 2019 | February | 13 | 16 | 10489.5 | 28500 | 36.81%
[29 empty] | 2019 | February | 13 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 13 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 13 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 13 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 13 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 13 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 13 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 14 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 14 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 14 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 14 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 14 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 14 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 14 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 14 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 14 | 8 | 9601.5 | 28500 | 33.69%
[29 empty] | 2019 | February | 14 | 9 | 21163.5 | 28500 | 74.26%
[29 empty] | 2019 | February | 14 | 10 | 31213 | 28500 | 109.5%
[29 empty] | 2019 | February | 14 | 11 | 36127 | 28500 | 126.8%
[29 empty] | 2019 | February | 14 | 12 | 37817 | 28500 | 132.7%
[29 empty] | 2019 | February | 14 | 13 | 36360 | 28500 | 127.6%
[29 empty] | 2019 | February | 14 | 14 | 30371.5 | 28500 | 106.6%
[29 empty] | 2019 | February | 14 | 15 | 23408.5 | 28500 | 82.14%
[29 empty] | 2019 | February | 14 | 16 | 10835.5 | 28500 | 38.02%
[29 empty] | 2019 | February | 14 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 14 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 14 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 14 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 14 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 14 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 14 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 15 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 15 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 15 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 15 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 15 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 15 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 15 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 15 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 15 | 8 | 10940.5 | 28500 | 38.39%
[29 empty] | 2019 | February | 15 | 9 | 21967.5 | 28500 | 77.08%
[29 empty] | 2019 | February | 15 | 10 | 32228.5 | 28500 | 113.1%
[29 empty] | 2019 | February | 15 | 11 | 37039 | 28500 | 130%
[29 empty] | 2019 | February | 15 | 12 | 38862.5 | 28500 | 136.4%
[29 empty] | 2019 | February | 15 | 13 | 37244.5 | 28500 | 130.7%
[29 empty] | 2019 | February | 15 | 14 | 30595 | 28500 | 107.4%
[29 empty] | 2019 | February | 15 | 15 | 23274 | 28500 | 81.66%
[29 empty] | 2019 | February | 15 | 16 | 11442.5 | 28500 | 40.15%
[29 empty] | 2019 | February | 15 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 15 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 15 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 15 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 15 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 15 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 15 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 16 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 16 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 16 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 16 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 16 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 16 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 16 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 16 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 16 | 8 | 278.5 | 28500 | 0.9772%
[29 empty] | 2019 | February | 16 | 9 | 3157.5 | 28500 | 11.08%
[29 empty] | 2019 | February | 16 | 10 | 3380 | 28500 | 11.86%
[29 empty] | 2019 | February | 16 | 11 | 4725.5 | 28500 | 16.58%
[29 empty] | 2019 | February | 16 | 12 | 4209.5 | 28500 | 14.77%
[29 empty] | 2019 | February | 16 | 13 | 4508 | 28500 | 15.82%
[29 empty] | 2019 | February | 16 | 14 | 2548 | 28500 | 8.94%
[29 empty] | 2019 | February | 16 | 15 | 3293 | 28500 | 11.55%
[29 empty] | 2019 | February | 16 | 16 | 1664.5 | 28500 | 5.84%
[29 empty] | 2019 | February | 16 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 16 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 16 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 16 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 16 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 16 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 16 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 17 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 17 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 17 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 17 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 17 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 17 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 17 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 17 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 17 | 8 | 11133 | 28500 | 39.06%
[29 empty] | 2019 | February | 17 | 9 | 15497.5 | 28500 | 54.38%
[29 empty] | 2019 | February | 17 | 10 | 31007 | 28500 | 108.8%
[29 empty] | 2019 | February | 17 | 11 | 37353.5 | 28500 | 131.1%
[29 empty] | 2019 | February | 17 | 12 | 39148.5 | 28500 | 137.4%
[29 empty] | 2019 | February | 17 | 13 | 37249.5 | 28500 | 130.7%
[29 empty] | 2019 | February | 17 | 14 | 28920.5 | 28500 | 101.5%
[29 empty] | 2019 | February | 17 | 15 | 22537 | 28500 | 79.08%
[29 empty] | 2019 | February | 17 | 16 | 3797 | 28500 | 13.32%
[29 empty] | 2019 | February | 17 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 17 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 17 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 17 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 17 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 17 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 17 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 18 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 18 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 18 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 18 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 18 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 18 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 18 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 18 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 18 | 8 | 518.5 | 28500 | 1.819%
[29 empty] | 2019 | February | 18 | 9 | 1618.5 | 28500 | 5.679%
[29 empty] | 2019 | February | 18 | 10 | 2167 | 28500 | 7.604%
[29 empty] | 2019 | February | 18 | 11 | 3346 | 28500 | 11.74%
[29 empty] | 2019 | February | 18 | 12 | 4641.5 | 28500 | 16.29%
[29 empty] | 2019 | February | 18 | 13 | 3311.5 | 28500 | 11.62%
[29 empty] | 2019 | February | 18 | 14 | 2093.5 | 28500 | 7.346%
[29 empty] | 2019 | February | 18 | 15 | 1686.5 | 28500 | 5.918%
[29 empty] | 2019 | February | 18 | 16 | 7258 | 28500 | 25.47%
[29 empty] | 2019 | February | 18 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 18 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 18 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 18 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 18 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 18 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 18 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 19 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 19 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 19 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 19 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 19 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 19 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 19 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 19 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 19 | 8 | 12188.5 | 28500 | 42.77%
[29 empty] | 2019 | February | 19 | 9 | 22967 | 28500 | 80.59%
[29 empty] | 2019 | February | 19 | 10 | 31636 | 28500 | 111%
[29 empty] | 2019 | February | 19 | 11 | 32863 | 28500 | 115.3%
[29 empty] | 2019 | February | 19 | 12 | 24475.5 | 28500 | 85.88%
[29 empty] | 2019 | February | 19 | 13 | 18740.5 | 28500 | 65.76%
[29 empty] | 2019 | February | 19 | 14 | 13648 | 28500 | 47.89%
[29 empty] | 2019 | February | 19 | 15 | 19021 | 28500 | 66.74%
[29 empty] | 2019 | February | 19 | 16 | 3375.5 | 28500 | 11.84%
[29 empty] | 2019 | February | 19 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 19 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 19 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 19 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 19 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 19 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 19 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 20 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 20 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 20 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 20 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 20 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 20 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 20 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 20 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 20 | 8 | 7484 | 28500 | 26.26%
[29 empty] | 2019 | February | 20 | 9 | 21983 | 28500 | 77.13%
[29 empty] | 2019 | February | 20 | 10 | 30576 | 28500 | 107.3%
[29 empty] | 2019 | February | 20 | 11 | 28062.5 | 28500 | 98.46%
[29 empty] | 2019 | February | 20 | 12 | 10363 | 28500 | 36.36%
[29 empty] | 2019 | February | 20 | 13 | 20085 | 28500 | 70.47%
[29 empty] | 2019 | February | 20 | 14 | 25847 | 28500 | 90.69%
[29 empty] | 2019 | February | 20 | 15 | 20363.5 | 28500 | 71.45%
[29 empty] | 2019 | February | 20 | 16 | 12527 | 28500 | 43.95%
[29 empty] | 2019 | February | 20 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 20 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 20 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 20 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 20 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 20 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 20 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 21 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 21 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 21 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 21 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 21 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 21 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 21 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 21 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 21 | 8 | 4334.5 | 28500 | 15.21%
[29 empty] | 2019 | February | 21 | 9 | 4803 | 28500 | 16.85%
[29 empty] | 2019 | February | 21 | 10 | 3782 | 28500 | 13.27%
[29 empty] | 2019 | February | 21 | 11 | 21926 | 28500 | 76.93%
[29 empty] | 2019 | February | 21 | 12 | 33182 | 28500 | 116.4%
[29 empty] | 2019 | February | 21 | 13 | 34824.5 | 28500 | 122.2%
[29 empty] | 2019 | February | 21 | 14 | 28513.5 | 28500 | 100%
[29 empty] | 2019 | February | 21 | 15 | 22150.5 | 28500 | 77.72%
[29 empty] | 2019 | February | 21 | 16 | 12060 | 28500 | 42.32%
[29 empty] | 2019 | February | 21 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 21 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 21 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 21 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 21 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 21 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 21 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 22 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 22 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 22 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 22 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 22 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 22 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 22 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 22 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 22 | 8 | 6676 | 28500 | 23.42%
[29 empty] | 2019 | February | 22 | 9 | 13345 | 28500 | 46.82%
[29 empty] | 2019 | February | 22 | 10 | 23626 | 28500 | 82.9%
[29 empty] | 2019 | February | 22 | 11 | 27544.5 | 28500 | 96.65%
[29 empty] | 2019 | February | 22 | 12 | 33545.5 | 28500 | 117.7%
[29 empty] | 2019 | February | 22 | 13 | 30326.5 | 28500 | 106.4%
[29 empty] | 2019 | February | 22 | 14 | 30676 | 28500 | 107.6%
[29 empty] | 2019 | February | 22 | 15 | 22565 | 28500 | 79.18%
[29 empty] | 2019 | February | 22 | 16 | 12377.5 | 28500 | 43.43%
[29 empty] | 2019 | February | 22 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 22 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 22 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 22 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 22 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 22 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 22 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 23 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 23 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 23 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 23 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 23 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 23 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 23 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 23 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 23 | 8 | 10751 | 28500 | 37.72%
[29 empty] | 2019 | February | 23 | 9 | 21876 | 28500 | 76.76%
[29 empty] | 2019 | February | 23 | 10 | 30457.5 | 28500 | 106.9%
[29 empty] | 2019 | February | 23 | 11 | 35196 | 28500 | 123.5%
[29 empty] | 2019 | February | 23 | 12 | 38722 | 28500 | 135.9%
[29 empty] | 2019 | February | 23 | 13 | 35573 | 28500 | 124.8%
[29 empty] | 2019 | February | 23 | 14 | 31503.5 | 28500 | 110.5%
[29 empty] | 2019 | February | 23 | 15 | 23240.5 | 28500 | 81.55%
[29 empty] | 2019 | February | 23 | 16 | 13123 | 28500 | 46.05%
[29 empty] | 2019 | February | 23 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 23 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 23 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 23 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 23 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 23 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 23 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 24 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 24 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 24 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 24 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 24 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 24 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 24 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 24 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 24 | 8 | 14262.5 | 28500 | 50.04%
[29 empty] | 2019 | February | 24 | 9 | 23213 | 28500 | 81.45%
[29 empty] | 2019 | February | 24 | 10 | 30897.5 | 28500 | 108.4%
[29 empty] | 2019 | February | 24 | 11 | 36515 | 28500 | 128.1%
[29 empty] | 2019 | February | 24 | 12 | 39388.5 | 28500 | 138.2%
[29 empty] | 2019 | February | 24 | 13 | 36804 | 28500 | 129.1%
[29 empty] | 2019 | February | 24 | 14 | 32785.5 | 28500 | 115%
[29 empty] | 2019 | February | 24 | 15 | 24947.5 | 28500 | 87.54%
[29 empty] | 2019 | February | 24 | 16 | 14685 | 28500 | 51.53%
[29 empty] | 2019 | February | 24 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 24 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 24 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 24 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 24 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 24 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 24 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 25 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 25 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 25 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 25 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 25 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 25 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 25 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 25 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 25 | 8 | 14015 | 28500 | 49.18%
[29 empty] | 2019 | February | 25 | 9 | 24363 | 28500 | 85.48%
[29 empty] | 2019 | February | 25 | 10 | 31438.5 | 28500 | 110.3%
[29 empty] | 2019 | February | 25 | 11 | 35468 | 28500 | 124.4%
[29 empty] | 2019 | February | 25 | 12 | 36195 | 28500 | 127%
[29 empty] | 2019 | February | 25 | 13 | 35316 | 28500 | 123.9%
[29 empty] | 2019 | February | 25 | 14 | 31424 | 28500 | 110.3%
[29 empty] | 2019 | February | 25 | 15 | 23730 | 28500 | 83.26%
[29 empty] | 2019 | February | 25 | 16 | 13677 | 28500 | 47.99%
[29 empty] | 2019 | February | 25 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 25 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 25 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 25 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 25 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 25 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 25 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 26 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 26 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 26 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 26 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 26 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 26 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 26 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 26 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 26 | 8 | 14108 | 28500 | 49.5%
[29 empty] | 2019 | February | 26 | 9 | 24638.5 | 28500 | 86.45%
[29 empty] | 2019 | February | 26 | 10 | 32023 | 28500 | 112.4%
[29 empty] | 2019 | February | 26 | 11 | 35938 | 28500 | 126.1%
[29 empty] | 2019 | February | 26 | 12 | 36512 | 28500 | 128.1%
[29 empty] | 2019 | February | 26 | 13 | 35869 | 28500 | 125.9%
[29 empty] | 2019 | February | 26 | 14 | 31841.5 | 28500 | 111.7%
[29 empty] | 2019 | February | 26 | 15 | 24278.5 | 28500 | 85.19%
[29 empty] | 2019 | February | 26 | 16 | 14565 | 28500 | 51.11%
[29 empty] | 2019 | February | 26 | 17 | 179.5 | 28500 | 0.6298%
[29 empty] | 2019 | February | 26 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 26 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 26 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 26 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 26 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 26 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 27 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 27 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 27 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 27 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 27 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 27 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 27 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 27 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 27 | 8 | 13766.5 | 28500 | 48.3%
[29 empty] | 2019 | February | 27 | 9 | 24474.5 | 28500 | 85.88%
[29 empty] | 2019 | February | 27 | 10 | 31294.5 | 28500 | 109.8%
[29 empty] | 2019 | February | 27 | 11 | 35279 | 28500 | 123.8%
[29 empty] | 2019 | February | 27 | 12 | 36219.5 | 28500 | 127.1%
[29 empty] | 2019 | February | 27 | 13 | 35746.5 | 28500 | 125.4%
[29 empty] | 2019 | February | 27 | 14 | 32049.5 | 28500 | 112.5%
[29 empty] | 2019 | February | 27 | 15 | 24193 | 28500 | 84.89%
[29 empty] | 2019 | February | 27 | 16 | 14188 | 28500 | 49.78%
[29 empty] | 2019 | February | 27 | 17 | 115.5 | 28500 | 0.4053%
[29 empty] | 2019 | February | 27 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 27 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 27 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 27 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 27 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 27 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 28 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 28 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 28 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 28 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 28 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 28 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 28 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 28 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 28 | 8 | 10856 | 28500 | 38.09%
[29 empty] | 2019 | February | 28 | 9 | 3546 | 28500 | 12.44%
[29 empty] | 2019 | February | 28 | 10 | 4051.5 | 28500 | 14.22%
[29 empty] | 2019 | February | 28 | 11 | 2460.5 | 28500 | 8.633%
[29 empty] | 2019 | February | 28 | 12 | 1385.5 | 28500 | 4.861%
[29 empty] | 2019 | February | 28 | 13 | 3013 | 28500 | 10.57%
[29 empty] | 2019 | February | 28 | 14 | 7020.5 | 28500 | 24.63%
[29 empty] | 2019 | February | 28 | 15 | 539 | 28500 | 1.891%
[29 empty] | 2019 | February | 28 | 16 | 1210 | 28500 | 4.246%
[29 empty] | 2019 | February | 28 | 17 | 13.5 | 28500 | 0.04737%
[29 empty] | 2019 | February | 28 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 28 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 28 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 28 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 28 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | February | 28 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 1 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 1 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 1 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 1 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 1 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 1 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 1 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 1 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 1 | 8 | 1333 | 28500 | 4.677%
[29 empty] | 2019 | March | 1 | 9 | 1992.5 | 28500 | 6.991%
[29 empty] | 2019 | March | 1 | 10 | 2826 | 28500 | 9.916%
[29 empty] | 2019 | March | 1 | 11 | 3363.5 | 28500 | 11.8%
[29 empty] | 2019 | March | 1 | 12 | 1537.5 | 28500 | 5.395%
[29 empty] | 2019 | March | 1 | 13 | 13205.5 | 28500 | 46.34%
[29 empty] | 2019 | March | 1 | 14 | 4077 | 28500 | 14.31%
[29 empty] | 2019 | March | 1 | 15 | 2342.5 | 28500 | 8.219%
[29 empty] | 2019 | March | 1 | 16 | 1316.5 | 28500 | 4.619%
[29 empty] | 2019 | March | 1 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 1 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 1 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 1 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 1 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 1 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 1 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 2 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 2 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 2 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 2 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 2 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 2 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 2 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 2 | 7 | 293 | 28500 | 1.028%
[29 empty] | 2019 | March | 2 | 8 | 3322 | 28500 | 11.66%
[29 empty] | 2019 | March | 2 | 9 | 3612 | 28500 | 12.67%
[29 empty] | 2019 | March | 2 | 10 | 3195 | 28500 | 11.21%
[29 empty] | 2019 | March | 2 | 11 | 3807 | 28500 | 13.36%
[29 empty] | 2019 | March | 2 | 12 | 6166 | 28500 | 21.64%
[29 empty] | 2019 | March | 2 | 13 | 11519.5 | 28500 | 40.42%
[29 empty] | 2019 | March | 2 | 14 | 23203.5 | 28500 | 81.42%
[29 empty] | 2019 | March | 2 | 15 | 11260 | 28500 | 39.51%
[29 empty] | 2019 | March | 2 | 16 | 1670 | 28500 | 5.86%
[29 empty] | 2019 | March | 2 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 2 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 2 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 2 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 2 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 2 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 2 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 3 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 3 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 3 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 3 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 3 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 3 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 3 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 3 | 7 | 51.5 | 28500 | 0.1807%
[29 empty] | 2019 | March | 3 | 8 | 605.5 | 28500 | 2.125%
[29 empty] | 2019 | March | 3 | 9 | 1862 | 28500 | 6.533%
[29 empty] | 2019 | March | 3 | 10 | 2383.5 | 28500 | 8.363%
[29 empty] | 2019 | March | 3 | 11 | 2918.5 | 28500 | 10.24%
[29 empty] | 2019 | March | 3 | 12 | 1174.5 | 28500 | 4.121%
[29 empty] | 2019 | March | 3 | 13 | 2418.5 | 28500 | 8.486%
[29 empty] | 2019 | March | 3 | 14 | 4189 | 28500 | 14.7%
[29 empty] | 2019 | March | 3 | 15 | 5390 | 28500 | 18.91%
[29 empty] | 2019 | March | 3 | 16 | 632.5 | 28500 | 2.219%
[29 empty] | 2019 | March | 3 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 3 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 3 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 3 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 3 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 3 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 3 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 4 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 4 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 4 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 4 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 4 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 4 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 4 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 4 | 7 | 228 | 28500 | 0.8%
[29 empty] | 2019 | March | 4 | 8 | 3559 | 28500 | 12.49%
[29 empty] | 2019 | March | 4 | 9 | 10066 | 28500 | 35.32%
[29 empty] | 2019 | March | 4 | 10 | 14591.5 | 28500 | 51.2%
[29 empty] | 2019 | March | 4 | 11 | 24406 | 28500 | 85.64%
[29 empty] | 2019 | March | 4 | 12 | 17126 | 28500 | 60.09%
[29 empty] | 2019 | March | 4 | 13 | 19300.5 | 28500 | 67.72%
[29 empty] | 2019 | March | 4 | 14 | 7917.5 | 28500 | 27.78%
[29 empty] | 2019 | March | 4 | 15 | 23786.5 | 28500 | 83.46%
[29 empty] | 2019 | March | 4 | 16 | 711 | 28500 | 2.495%
[29 empty] | 2019 | March | 4 | 17 | 822 | 28500 | 2.884%
[29 empty] | 2019 | March | 4 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 4 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 4 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 4 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 4 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 4 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 5 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 5 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 5 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 5 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 5 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 5 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 5 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 5 | 7 | 959.5 | 28500 | 3.367%
[29 empty] | 2019 | March | 5 | 8 | 15835.5 | 28500 | 55.56%
[29 empty] | 2019 | March | 5 | 9 | 27219.5 | 28500 | 95.51%
[29 empty] | 2019 | March | 5 | 10 | 34806.5 | 28500 | 122.1%
[29 empty] | 2019 | March | 5 | 11 | 36360 | 28500 | 127.6%
[29 empty] | 2019 | March | 5 | 12 | 25560.5 | 28500 | 89.69%
[29 empty] | 2019 | March | 5 | 13 | 20784.5 | 28500 | 72.93%
[29 empty] | 2019 | March | 5 | 14 | 18297.5 | 28500 | 64.2%
[29 empty] | 2019 | March | 5 | 15 | 19359 | 28500 | 67.93%
[29 empty] | 2019 | March | 5 | 16 | 6808 | 28500 | 23.89%
[29 empty] | 2019 | March | 5 | 17 | 304 | 28500 | 1.067%
[29 empty] | 2019 | March | 5 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 5 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 5 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 5 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 5 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 5 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 6 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 6 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 6 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 6 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 6 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 6 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 6 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 6 | 7 | 32 | 28500 | 0.1123%
[29 empty] | 2019 | March | 6 | 8 | 2899 | 28500 | 10.17%
[29 empty] | 2019 | March | 6 | 9 | 3218 | 28500 | 11.29%
[29 empty] | 2019 | March | 6 | 10 | 7132.5 | 28500 | 25.03%
[29 empty] | 2019 | March | 6 | 11 | 6839 | 28500 | 24%
[29 empty] | 2019 | March | 6 | 12 | 4067 | 28500 | 14.27%
[29 empty] | 2019 | March | 6 | 13 | 10577.5 | 28500 | 37.11%
[29 empty] | 2019 | March | 6 | 14 | 3949.5 | 28500 | 13.86%
[29 empty] | 2019 | March | 6 | 15 | 3653 | 28500 | 12.82%
[29 empty] | 2019 | March | 6 | 16 | 2703.5 | 28500 | 9.486%
[29 empty] | 2019 | March | 6 | 17 | 328.5 | 28500 | 1.153%
[29 empty] | 2019 | March | 6 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 6 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 6 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 6 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 6 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 6 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 7 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 7 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 7 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 7 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 7 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 7 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 7 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 7 | 7 | 1169.5 | 28500 | 4.104%
[29 empty] | 2019 | March | 7 | 8 | 16178.5 | 28500 | 56.77%
[29 empty] | 2019 | March | 7 | 9 | 27279.5 | 28500 | 95.72%
[29 empty] | 2019 | March | 7 | 10 | 11887.5 | 28500 | 41.71%
[29 empty] | 2019 | March | 7 | 11 | 35664 | 28500 | 125.1%
[29 empty] | 2019 | March | 7 | 12 | 17414 | 28500 | 61.1%
[29 empty] | 2019 | March | 7 | 13 | 32240 | 28500 | 113.1%
[29 empty] | 2019 | March | 7 | 14 | 14378.5 | 28500 | 50.45%
[29 empty] | 2019 | March | 7 | 15 | 11085.5 | 28500 | 38.9%
[29 empty] | 2019 | March | 7 | 16 | 6174 | 28500 | 21.66%
[29 empty] | 2019 | March | 7 | 17 | 472 | 28500 | 1.656%
[29 empty] | 2019 | March | 7 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 7 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 7 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 7 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 7 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 7 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 8 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 8 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 8 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 8 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 8 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 8 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 8 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 8 | 7 | 1263 | 28500 | 4.432%
[29 empty] | 2019 | March | 8 | 8 | 12375 | 28500 | 43.42%
[29 empty] | 2019 | March | 8 | 9 | 22483 | 28500 | 78.89%
[29 empty] | 2019 | March | 8 | 10 | 30393 | 28500 | 106.6%
[29 empty] | 2019 | March | 8 | 11 | 20316.5 | 28500 | 71.29%
[29 empty] | 2019 | March | 8 | 12 | 6949 | 28500 | 24.38%
[29 empty] | 2019 | March | 8 | 13 | 5614.5 | 28500 | 19.7%
[29 empty] | 2019 | March | 8 | 14 | 5312 | 28500 | 18.64%
[29 empty] | 2019 | March | 8 | 15 | 2860.5 | 28500 | 10.04%
[29 empty] | 2019 | March | 8 | 16 | 2306.5 | 28500 | 8.093%
[29 empty] | 2019 | March | 8 | 17 | 120.5 | 28500 | 0.4228%
[29 empty] | 2019 | March | 8 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 8 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 8 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 8 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 8 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 8 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 9 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 9 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 9 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 9 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 9 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 9 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 9 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 9 | 7 | 964.5 | 28500 | 3.384%
[29 empty] | 2019 | March | 9 | 8 | 1598.5 | 28500 | 5.609%
[29 empty] | 2019 | March | 9 | 9 | 27088.5 | 28500 | 95.05%
[29 empty] | 2019 | March | 9 | 10 | 4519.5 | 28500 | 15.86%
[29 empty] | 2019 | March | 9 | 11 | 18607 | 28500 | 65.29%
[29 empty] | 2019 | March | 9 | 12 | 35346.5 | 28500 | 124%
[29 empty] | 2019 | March | 9 | 13 | 32006.5 | 28500 | 112.3%
[29 empty] | 2019 | March | 9 | 14 | 26528.5 | 28500 | 93.08%
[29 empty] | 2019 | March | 9 | 15 | 15449 | 28500 | 54.21%
[29 empty] | 2019 | March | 9 | 16 | 5620.5 | 28500 | 19.72%
[29 empty] | 2019 | March | 9 | 17 | 728 | 28500 | 2.554%
[29 empty] | 2019 | March | 9 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 9 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 9 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 9 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 9 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 9 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 10 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 10 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 10 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 10 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 10 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 10 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 10 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 10 | 7 | 2182.5 | 28500 | 7.658%
[29 empty] | 2019 | March | 10 | 8 | 3226.5 | 28500 | 11.32%
[29 empty] | 2019 | March | 10 | 9 | 25370.5 | 28500 | 89.02%
[29 empty] | 2019 | March | 10 | 10 | 28938.5 | 28500 | 101.5%
[29 empty] | 2019 | March | 10 | 11 | 4297.5 | 28500 | 15.08%
[29 empty] | 2019 | March | 10 | 12 | 2297.5 | 28500 | 8.061%
[29 empty] | 2019 | March | 10 | 13 | 38854.5 | 28500 | 136.3%
[29 empty] | 2019 | March | 10 | 14 | 35323.5 | 28500 | 123.9%
[29 empty] | 2019 | March | 10 | 15 | 8921.5 | 28500 | 31.3%
[29 empty] | 2019 | March | 10 | 16 | 16281 | 28500 | 57.13%
[29 empty] | 2019 | March | 10 | 17 | 4338.5 | 28500 | 15.22%
[29 empty] | 2019 | March | 10 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 10 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 10 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 10 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 10 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 10 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 11 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 11 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 11 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 11 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 11 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 11 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 11 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 11 | 7 | 4931 | 28500 | 17.3%
[29 empty] | 2019 | March | 11 | 8 | 17677.5 | 28500 | 62.03%
[29 empty] | 2019 | March | 11 | 9 | 27430.5 | 28500 | 96.25%
[29 empty] | 2019 | March | 11 | 10 | 35076 | 28500 | 123.1%
[29 empty] | 2019 | March | 11 | 11 | 37785 | 28500 | 132.6%
[29 empty] | 2019 | March | 11 | 12 | 42733.5 | 28500 | 149.9%
[29 empty] | 2019 | March | 11 | 13 | 38057 | 28500 | 133.5%
[29 empty] | 2019 | March | 11 | 14 | 25402.5 | 28500 | 89.13%
[29 empty] | 2019 | March | 11 | 15 | 24995.5 | 28500 | 87.7%
[29 empty] | 2019 | March | 11 | 16 | 17191 | 28500 | 60.32%
[29 empty] | 2019 | March | 11 | 17 | 2864 | 28500 | 10.05%
[29 empty] | 2019 | March | 11 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 11 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 11 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 11 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 11 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 11 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 12 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 12 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 12 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 12 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 12 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 12 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 12 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 12 | 7 | 223.5 | 28500 | 0.7842%
[29 empty] | 2019 | March | 12 | 8 | 1299 | 28500 | 4.558%
[29 empty] | 2019 | March | 12 | 9 | 2222 | 28500 | 7.796%
[29 empty] | 2019 | March | 12 | 10 | 3733.5 | 28500 | 13.1%
[29 empty] | 2019 | March | 12 | 11 | 4885 | 28500 | 17.14%
[29 empty] | 2019 | March | 12 | 12 | 3887.5 | 28500 | 13.64%
[29 empty] | 2019 | March | 12 | 13 | 2829.5 | 28500 | 9.928%
[29 empty] | 2019 | March | 12 | 14 | 2951 | 28500 | 10.35%
[29 empty] | 2019 | March | 12 | 15 | 1653 | 28500 | 5.8%
[29 empty] | 2019 | March | 12 | 16 | 595 | 28500 | 2.088%
[29 empty] | 2019 | March | 12 | 17 | 1802 | 28500 | 6.323%
[29 empty] | 2019 | March | 12 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 12 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 12 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 12 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 12 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 12 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 13 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 13 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 13 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 13 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 13 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 13 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 13 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 13 | 7 | 4448 | 28500 | 15.61%
[29 empty] | 2019 | March | 13 | 8 | 13947 | 28500 | 48.94%
[29 empty] | 2019 | March | 13 | 9 | 6582.5 | 28500 | 23.1%
[29 empty] | 2019 | March | 13 | 10 | 4524 | 28500 | 15.87%
[29 empty] | 2019 | March | 13 | 11 | 6405.5 | 28500 | 22.48%
[29 empty] | 2019 | March | 13 | 12 | 29944.5 | 28500 | 105.1%
[29 empty] | 2019 | March | 13 | 13 | 5254 | 28500 | 18.44%
[29 empty] | 2019 | March | 13 | 14 | 3002.5 | 28500 | 10.54%
[29 empty] | 2019 | March | 13 | 15 | 2426 | 28500 | 8.512%
[29 empty] | 2019 | March | 13 | 16 | 4024.5 | 28500 | 14.12%
[29 empty] | 2019 | March | 13 | 17 | 1882 | 28500 | 6.604%
[29 empty] | 2019 | March | 13 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 13 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 13 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 13 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 13 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 13 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 14 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 14 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 14 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 14 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 14 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 14 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 14 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 14 | 7 | 613.5 | 28500 | 2.153%
[29 empty] | 2019 | March | 14 | 8 | 4600 | 28500 | 16.14%
[29 empty] | 2019 | March | 14 | 9 | 6579.5 | 28500 | 23.09%
[29 empty] | 2019 | March | 14 | 10 | 9886.5 | 28500 | 34.69%
[29 empty] | 2019 | March | 14 | 11 | 1927.5 | 28500 | 6.763%
[29 empty] | 2019 | March | 14 | 12 | 6385.5 | 28500 | 22.41%
[29 empty] | 2019 | March | 14 | 13 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 14 | 14 | 26679.5 | 28500 | 93.61%
[29 empty] | 2019 | March | 14 | 15 | 5631.5 | 28500 | 19.76%
[29 empty] | 2019 | March | 14 | 16 | 14616.5 | 28500 | 51.29%
[29 empty] | 2019 | March | 14 | 17 | 4415.5 | 28500 | 15.49%
[29 empty] | 2019 | March | 14 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 14 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 14 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 14 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 14 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 14 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 15 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 15 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 15 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 15 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 15 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 15 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 15 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 15 | 7 | 666.5 | 28500 | 2.339%
[29 empty] | 2019 | March | 15 | 8 | 3762 | 28500 | 13.2%
[29 empty] | 2019 | March | 15 | 9 | 5607 | 28500 | 19.67%
[29 empty] | 2019 | March | 15 | 10 | 15576.5 | 28500 | 54.65%
[29 empty] | 2019 | March | 15 | 11 | 6149 | 28500 | 21.58%
[29 empty] | 2019 | March | 15 | 12 | 3814.5 | 28500 | 13.38%
[29 empty] | 2019 | March | 15 | 13 | 5617.5 | 28500 | 19.71%
[29 empty] | 2019 | March | 15 | 14 | 5383 | 28500 | 18.89%
[29 empty] | 2019 | March | 15 | 15 | 3622.5 | 28500 | 12.71%
[29 empty] | 2019 | March | 15 | 16 | 6336 | 28500 | 22.23%
[29 empty] | 2019 | March | 15 | 17 | 1532 | 28500 | 5.375%
[29 empty] | 2019 | March | 15 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 15 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 15 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 15 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 15 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 15 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 16 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 16 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 16 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 16 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 16 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 16 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 16 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 16 | 7 | 1038 | 28500 | 3.642%
[29 empty] | 2019 | March | 16 | 8 | 1392.5 | 28500 | 4.886%
[29 empty] | 2019 | March | 16 | 9 | 2391.5 | 28500 | 8.391%
[29 empty] | 2019 | March | 16 | 10 | 4012.5 | 28500 | 14.08%
[29 empty] | 2019 | March | 16 | 11 | 4441.5 | 28500 | 15.58%
[29 empty] | 2019 | March | 16 | 12 | 3653 | 28500 | 12.82%
[29 empty] | 2019 | March | 16 | 13 | 1820 | 28500 | 6.386%
[29 empty] | 2019 | March | 16 | 14 | 3647 | 28500 | 12.8%
[29 empty] | 2019 | March | 16 | 15 | 2121 | 28500 | 7.442%
[29 empty] | 2019 | March | 16 | 16 | 4307.5 | 28500 | 15.11%
[29 empty] | 2019 | March | 16 | 17 | 142.5 | 28500 | 0.5%
[29 empty] | 2019 | March | 16 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 16 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 16 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 16 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 16 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 16 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 17 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 17 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 17 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 17 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 17 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 17 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 17 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 17 | 7 | 6455.5 | 28500 | 22.65%
[29 empty] | 2019 | March | 17 | 8 | 19307 | 28500 | 67.74%
[29 empty] | 2019 | March | 17 | 9 | 23006.5 | 28500 | 80.72%
[29 empty] | 2019 | March | 17 | 10 | 22660 | 28500 | 79.51%
[29 empty] | 2019 | March | 17 | 11 | 2776 | 28500 | 9.74%
[29 empty] | 2019 | March | 17 | 12 | 42087.5 | 28500 | 147.7%
[29 empty] | 2019 | March | 17 | 13 | 30515 | 28500 | 107.1%
[29 empty] | 2019 | March | 17 | 14 | 21558 | 28500 | 75.64%
[29 empty] | 2019 | March | 17 | 15 | 23695 | 28500 | 83.14%
[29 empty] | 2019 | March | 17 | 16 | 2637.5 | 28500 | 9.254%
[29 empty] | 2019 | March | 17 | 17 | 5507 | 28500 | 19.32%
[29 empty] | 2019 | March | 17 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 17 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 17 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 17 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 17 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 17 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 18 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 18 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 18 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 18 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 18 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 18 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 18 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 18 | 7 | 1385 | 28500 | 4.86%
[29 empty] | 2019 | March | 18 | 8 | 15417 | 28500 | 54.09%
[29 empty] | 2019 | March | 18 | 9 | 21816 | 28500 | 76.55%
[29 empty] | 2019 | March | 18 | 10 | 10687.5 | 28500 | 37.5%
[29 empty] | 2019 | March | 18 | 11 | 31919.5 | 28500 | 112%
[29 empty] | 2019 | March | 18 | 12 | 13307.5 | 28500 | 46.69%
[29 empty] | 2019 | March | 18 | 13 | 23659 | 28500 | 83.01%
[29 empty] | 2019 | March | 18 | 14 | 22591 | 28500 | 79.27%
[29 empty] | 2019 | March | 18 | 15 | 9732.5 | 28500 | 34.15%
[29 empty] | 2019 | March | 18 | 16 | 15814 | 28500 | 55.49%
[29 empty] | 2019 | March | 18 | 17 | 4869.5 | 28500 | 17.09%
[29 empty] | 2019 | March | 18 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 18 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 18 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 18 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 18 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 18 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 19 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 19 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 19 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 19 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 19 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 19 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 19 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 19 | 7 | 1903.5 | 28500 | 6.679%
[29 empty] | 2019 | March | 19 | 8 | 4674.5 | 28500 | 16.4%
[29 empty] | 2019 | March | 19 | 9 | 22862 | 28500 | 80.22%
[29 empty] | 2019 | March | 19 | 10 | 8993.5 | 28500 | 31.56%
[29 empty] | 2019 | March | 19 | 11 | 18077 | 28500 | 63.43%
[29 empty] | 2019 | March | 19 | 12 | 12540.5 | 28500 | 44%
[29 empty] | 2019 | March | 19 | 13 | 15694 | 28500 | 55.07%
[29 empty] | 2019 | March | 19 | 14 | 4129 | 28500 | 14.49%
[29 empty] | 2019 | March | 19 | 15 | 3892 | 28500 | 13.66%
[29 empty] | 2019 | March | 19 | 16 | 4657 | 28500 | 16.34%
[29 empty] | 2019 | March | 19 | 17 | 1157 | 28500 | 4.06%
[29 empty] | 2019 | March | 19 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 19 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 19 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 19 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 19 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 19 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 20 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 20 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 20 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 20 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 20 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 20 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 20 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 20 | 7 | 3720.5 | 28500 | 13.05%
[29 empty] | 2019 | March | 20 | 8 | 6851.5 | 28500 | 24.04%
[29 empty] | 2019 | March | 20 | 9 | 3471.5 | 28500 | 12.18%
[29 empty] | 2019 | March | 20 | 10 | 5498.5 | 28500 | 19.29%
[29 empty] | 2019 | March | 20 | 11 | 3714 | 28500 | 13.03%
[29 empty] | 2019 | March | 20 | 12 | 3277 | 28500 | 11.5%
[29 empty] | 2019 | March | 20 | 13 | 4236 | 28500 | 14.86%
[29 empty] | 2019 | March | 20 | 14 | 5629 | 28500 | 19.75%
[29 empty] | 2019 | March | 20 | 15 | 4028.5 | 28500 | 14.14%
[29 empty] | 2019 | March | 20 | 16 | 3762 | 28500 | 13.2%
[29 empty] | 2019 | March | 20 | 17 | 1082 | 28500 | 3.796%
[29 empty] | 2019 | March | 20 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 20 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 20 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 20 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 20 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 20 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 21 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 21 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 21 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 21 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 21 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 21 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 21 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 21 | 7 | 2790 | 28500 | 9.789%
[29 empty] | 2019 | March | 21 | 8 | 5413 | 28500 | 18.99%
[29 empty] | 2019 | March | 21 | 9 | 8255 | 28500 | 28.96%
[29 empty] | 2019 | March | 21 | 10 | 11670.5 | 28500 | 40.95%
[29 empty] | 2019 | March | 21 | 11 | 9401.5 | 28500 | 32.99%
[29 empty] | 2019 | March | 21 | 12 | 5440.5 | 28500 | 19.09%
[29 empty] | 2019 | March | 21 | 13 | 3950.5 | 28500 | 13.86%
[29 empty] | 2019 | March | 21 | 14 | 6516 | 28500 | 22.86%
[29 empty] | 2019 | March | 21 | 15 | 7207 | 28500 | 25.29%
[29 empty] | 2019 | March | 21 | 16 | 4364.5 | 28500 | 15.31%
[29 empty] | 2019 | March | 21 | 17 | 1272.5 | 28500 | 4.465%
[29 empty] | 2019 | March | 21 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 21 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 21 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 21 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 21 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 21 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 22 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 22 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 22 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 22 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 22 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 22 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 22 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 22 | 7 | 1851 | 28500 | 6.495%
[29 empty] | 2019 | March | 22 | 8 | 3055 | 28500 | 10.72%
[29 empty] | 2019 | March | 22 | 9 | 2958.5 | 28500 | 10.38%
[29 empty] | 2019 | March | 22 | 10 | 2908.5 | 28500 | 10.21%
[29 empty] | 2019 | March | 22 | 11 | 3676 | 28500 | 12.9%
[29 empty] | 2019 | March | 22 | 12 | 3358.5 | 28500 | 11.78%
[29 empty] | 2019 | March | 22 | 13 | 3468.5 | 28500 | 12.17%
[29 empty] | 2019 | March | 22 | 14 | 2927.5 | 28500 | 10.27%
[29 empty] | 2019 | March | 22 | 15 | 2700 | 28500 | 9.474%
[29 empty] | 2019 | March | 22 | 16 | 2441.5 | 28500 | 8.567%
[29 empty] | 2019 | March | 22 | 17 | 1031 | 28500 | 3.618%
[29 empty] | 2019 | March | 22 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 22 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 22 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 22 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 22 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 22 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 23 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 23 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 23 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 23 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 23 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 23 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 23 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 23 | 7 | 807 | 28500 | 2.832%
[29 empty] | 2019 | March | 23 | 8 | 1042.5 | 28500 | 3.658%
[29 empty] | 2019 | March | 23 | 9 | 7317.5 | 28500 | 25.68%
[29 empty] | 2019 | March | 23 | 10 | 9762 | 28500 | 34.25%
[29 empty] | 2019 | March | 23 | 11 | 15798 | 28500 | 55.43%
[29 empty] | 2019 | March | 23 | 12 | 19383 | 28500 | 68.01%
[29 empty] | 2019 | March | 23 | 13 | 15316.5 | 28500 | 53.74%
[29 empty] | 2019 | March | 23 | 14 | 9892 | 28500 | 34.71%
[29 empty] | 2019 | March | 23 | 15 | 11862.5 | 28500 | 41.62%
[29 empty] | 2019 | March | 23 | 16 | 10006 | 28500 | 35.11%
[29 empty] | 2019 | March | 23 | 17 | 3924 | 28500 | 13.77%
[29 empty] | 2019 | March | 23 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 23 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 23 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 23 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 23 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 23 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 24 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 24 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 24 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 24 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 24 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 24 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 24 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 24 | 7 | 6363.5 | 28500 | 22.33%
[29 empty] | 2019 | March | 24 | 8 | 19605.5 | 28500 | 68.79%
[29 empty] | 2019 | March | 24 | 9 | 29994 | 28500 | 105.2%
[29 empty] | 2019 | March | 24 | 10 | 36551 | 28500 | 128.2%
[29 empty] | 2019 | March | 24 | 11 | 41843.5 | 28500 | 146.8%
[29 empty] | 2019 | March | 24 | 12 | 43350.5 | 28500 | 152.1%
[29 empty] | 2019 | March | 24 | 13 | 41570 | 28500 | 145.9%
[29 empty] | 2019 | March | 24 | 14 | 35983 | 28500 | 126.3%
[29 empty] | 2019 | March | 24 | 15 | 28990.5 | 28500 | 101.7%
[29 empty] | 2019 | March | 24 | 16 | 18225 | 28500 | 63.95%
[29 empty] | 2019 | March | 24 | 17 | 5520.5 | 28500 | 19.37%
[29 empty] | 2019 | March | 24 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 24 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 24 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 24 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 24 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 24 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 25 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 25 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 25 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 25 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 25 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 25 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 25 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 25 | 7 | 7905 | 28500 | 27.74%
[29 empty] | 2019 | March | 25 | 8 | 20236 | 28500 | 71%
[29 empty] | 2019 | March | 25 | 9 | 31659.5 | 28500 | 111.1%
[29 empty] | 2019 | March | 25 | 10 | 35751.5 | 28500 | 125.4%
[29 empty] | 2019 | March | 25 | 11 | 36992.5 | 28500 | 129.8%
[29 empty] | 2019 | March | 25 | 12 | 43403.5 | 28500 | 152.3%
[29 empty] | 2019 | March | 25 | 13 | 39921.5 | 28500 | 140.1%
[29 empty] | 2019 | March | 25 | 14 | 34112.5 | 28500 | 119.7%
[29 empty] | 2019 | March | 25 | 15 | 27426 | 28500 | 96.23%
[29 empty] | 2019 | March | 25 | 16 | 18632 | 28500 | 65.38%
[29 empty] | 2019 | March | 25 | 17 | 5921 | 28500 | 20.78%
[29 empty] | 2019 | March | 25 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 25 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 25 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 25 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 25 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 25 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 26 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 26 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 26 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 26 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 26 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 26 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 26 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 26 | 7 | 6930.5 | 28500 | 24.32%
[29 empty] | 2019 | March | 26 | 8 | 13353 | 28500 | 46.85%
[29 empty] | 2019 | March | 26 | 9 | 29475 | 28500 | 103.4%
[29 empty] | 2019 | March | 26 | 10 | 36464.5 | 28500 | 127.9%
[29 empty] | 2019 | March | 26 | 11 | 40237 | 28500 | 141.2%
[29 empty] | 2019 | March | 26 | 12 | 42598.5 | 28500 | 149.5%
[29 empty] | 2019 | March | 26 | 13 | 14754.5 | 28500 | 51.77%
[29 empty] | 2019 | March | 26 | 14 | 13261.5 | 28500 | 46.53%
[29 empty] | 2019 | March | 26 | 15 | 19602 | 28500 | 68.78%
[29 empty] | 2019 | March | 26 | 16 | 9320 | 28500 | 32.7%
[29 empty] | 2019 | March | 26 | 17 | 5546 | 28500 | 19.46%
[29 empty] | 2019 | March | 26 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 26 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 26 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 26 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 26 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 26 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 27 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 27 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 27 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 27 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 27 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 27 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 27 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 27 | 7 | 3925 | 28500 | 13.77%
[29 empty] | 2019 | March | 27 | 8 | 7344.5 | 28500 | 25.77%
[29 empty] | 2019 | March | 27 | 9 | 9285 | 28500 | 32.58%
[29 empty] | 2019 | March | 27 | 10 | 9114 | 28500 | 31.98%
[29 empty] | 2019 | March | 27 | 11 | 13035.5 | 28500 | 45.74%
[29 empty] | 2019 | March | 27 | 12 | 4474.5 | 28500 | 15.7%
[29 empty] | 2019 | March | 27 | 13 | 5839.5 | 28500 | 20.49%
[29 empty] | 2019 | March | 27 | 14 | 4819.5 | 28500 | 16.91%
[29 empty] | 2019 | March | 27 | 15 | 10211 | 28500 | 35.83%
[29 empty] | 2019 | March | 27 | 16 | 8664 | 28500 | 30.4%
[29 empty] | 2019 | March | 27 | 17 | 3088 | 28500 | 10.84%
[29 empty] | 2019 | March | 27 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 27 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 27 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 27 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 27 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 27 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 28 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 28 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 28 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 28 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 28 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 28 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 28 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 28 | 7 | 2958 | 28500 | 10.38%
[29 empty] | 2019 | March | 28 | 8 | 5638 | 28500 | 19.78%
[29 empty] | 2019 | March | 28 | 9 | 6296 | 28500 | 22.09%
[29 empty] | 2019 | March | 28 | 10 | 11066 | 28500 | 38.83%
[29 empty] | 2019 | March | 28 | 11 | 24297 | 28500 | 85.25%
[29 empty] | 2019 | March | 28 | 12 | 21698 | 28500 | 76.13%
[29 empty] | 2019 | March | 28 | 13 | 25292 | 28500 | 88.74%
[29 empty] | 2019 | March | 28 | 14 | 30162 | 28500 | 105.8%
[29 empty] | 2019 | March | 28 | 15 | 26021 | 28500 | 91.3%
[29 empty] | 2019 | March | 28 | 16 | 17131 | 28500 | 60.11%
[29 empty] | 2019 | March | 28 | 17 | 5820 | 28500 | 20.42%
[29 empty] | 2019 | March | 28 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 28 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 28 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 28 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 28 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 28 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 29 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 29 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 29 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 29 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 29 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 29 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 29 | 6 | 203.5 | 28500 | 0.714%
[29 empty] | 2019 | March | 29 | 7 | 8284 | 28500 | 29.07%
[29 empty] | 2019 | March | 29 | 8 | 19594.5 | 28500 | 68.75%
[29 empty] | 2019 | March | 29 | 9 | 29087.5 | 28500 | 102.1%
[29 empty] | 2019 | March | 29 | 10 | 36257 | 28500 | 127.2%
[29 empty] | 2019 | March | 29 | 11 | 39239 | 28500 | 137.7%
[29 empty] | 2019 | March | 29 | 12 | 41504.5 | 28500 | 145.6%
[29 empty] | 2019 | March | 29 | 13 | 40252 | 28500 | 141.2%
[29 empty] | 2019 | March | 29 | 14 | 35399.5 | 28500 | 124.2%
[29 empty] | 2019 | March | 29 | 15 | 27294 | 28500 | 95.77%
[29 empty] | 2019 | March | 29 | 16 | 16396 | 28500 | 57.53%
[29 empty] | 2019 | March | 29 | 17 | 5739 | 28500 | 20.14%
[29 empty] | 2019 | March | 29 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 29 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 29 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 29 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 29 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 29 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 30 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 30 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 30 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 30 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 30 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 30 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 30 | 6 | 122.5 | 28500 | 0.4298%
[29 empty] | 2019 | March | 30 | 7 | 8002 | 28500 | 28.08%
[29 empty] | 2019 | March | 30 | 8 | 18703 | 28500 | 65.62%
[29 empty] | 2019 | March | 30 | 9 | 27969 | 28500 | 98.14%
[29 empty] | 2019 | March | 30 | 10 | 34872.5 | 28500 | 122.4%
[29 empty] | 2019 | March | 30 | 11 | 18254.5 | 28500 | 64.05%
[29 empty] | 2019 | March | 30 | 12 | 17455 | 28500 | 61.25%
[29 empty] | 2019 | March | 30 | 13 | 12303 | 28500 | 43.17%
[29 empty] | 2019 | March | 30 | 14 | 6368.5 | 28500 | 22.35%
[29 empty] | 2019 | March | 30 | 15 | 13958.5 | 28500 | 48.98%
[29 empty] | 2019 | March | 30 | 16 | 9946.5 | 28500 | 34.9%
[29 empty] | 2019 | March | 30 | 17 | 5310 | 28500 | 18.63%
[29 empty] | 2019 | March | 30 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 30 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 30 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 30 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 30 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 30 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 31 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 31 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 31 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 31 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 31 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 31 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 31 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 31 | 7 | 1979 | 28500 | 6.944%
[29 empty] | 2019 | March | 31 | 8 | 1845.5 | 28500 | 6.475%
[29 empty] | 2019 | March | 31 | 9 | 2942.5 | 28500 | 10.32%
[29 empty] | 2019 | March | 31 | 10 | 3716 | 28500 | 13.04%
[29 empty] | 2019 | March | 31 | 11 | 6414 | 28500 | 22.51%
[29 empty] | 2019 | March | 31 | 12 | 12421.5 | 28500 | 43.58%
[29 empty] | 2019 | March | 31 | 13 | 17547.5 | 28500 | 61.57%
[29 empty] | 2019 | March | 31 | 14 | 28249 | 28500 | 99.12%
[29 empty] | 2019 | March | 31 | 15 | 25964.5 | 28500 | 91.1%
[29 empty] | 2019 | March | 31 | 16 | 16640.5 | 28500 | 58.39%
[29 empty] | 2019 | March | 31 | 17 | 5944 | 28500 | 20.86%
[29 empty] | 2019 | March | 31 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 31 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 31 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 31 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 31 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | March | 31 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 1 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 1 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 1 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 1 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 1 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 1 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 1 | 6 | 312.5 | 28500 | 1.096%
[29 empty] | 2019 | April | 1 | 7 | 8047 | 28500 | 28.24%
[29 empty] | 2019 | April | 1 | 8 | 18576.5 | 28500 | 65.18%
[29 empty] | 2019 | April | 1 | 9 | 29966 | 28500 | 105.1%
[29 empty] | 2019 | April | 1 | 10 | 37115.5 | 28500 | 130.2%
[29 empty] | 2019 | April | 1 | 11 | 41110 | 28500 | 144.2%
[29 empty] | 2019 | April | 1 | 12 | 42336 | 28500 | 148.5%
[29 empty] | 2019 | April | 1 | 13 | 41324.5 | 28500 | 145%
[29 empty] | 2019 | April | 1 | 14 | 35370 | 28500 | 124.1%
[29 empty] | 2019 | April | 1 | 15 | 26722.5 | 28500 | 93.76%
[29 empty] | 2019 | April | 1 | 16 | 15210 | 28500 | 53.37%
[29 empty] | 2019 | April | 1 | 17 | 4903.5 | 28500 | 17.21%
[29 empty] | 2019 | April | 1 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 1 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 1 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 1 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 1 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 1 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 2 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 2 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 2 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 2 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 2 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 2 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 2 | 6 | 100.5 | 28500 | 0.3526%
[29 empty] | 2019 | April | 2 | 7 | 721.5 | 28500 | 2.532%
[29 empty] | 2019 | April | 2 | 8 | 1519 | 28500 | 5.33%
[29 empty] | 2019 | April | 2 | 9 | 6773 | 28500 | 23.76%
[29 empty] | 2019 | April | 2 | 10 | 6742 | 28500 | 23.66%
[29 empty] | 2019 | April | 2 | 11 | 2291 | 28500 | 8.039%
[29 empty] | 2019 | April | 2 | 12 | 4863.5 | 28500 | 17.06%
[29 empty] | 2019 | April | 2 | 13 | 10727.5 | 28500 | 37.64%
[29 empty] | 2019 | April | 2 | 14 | 12825 | 28500 | 45%
[29 empty] | 2019 | April | 2 | 15 | 17018.5 | 28500 | 59.71%
[29 empty] | 2019 | April | 2 | 16 | 646 | 28500 | 2.267%
[29 empty] | 2019 | April | 2 | 17 | 6198 | 28500 | 21.75%
[29 empty] | 2019 | April | 2 | 18 | 60 | 28500 | 0.2105%
[29 empty] | 2019 | April | 2 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 2 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 2 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 2 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 2 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 3 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 3 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 3 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 3 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 3 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 3 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 3 | 6 | 601 | 28500 | 2.109%
[29 empty] | 2019 | April | 3 | 7 | 7664.5 | 28500 | 26.89%
[29 empty] | 2019 | April | 3 | 8 | 18636 | 28500 | 65.39%
[29 empty] | 2019 | April | 3 | 9 | 17909 | 28500 | 62.84%
[29 empty] | 2019 | April | 3 | 10 | 12344 | 28500 | 43.31%
[29 empty] | 2019 | April | 3 | 11 | 19947.5 | 28500 | 69.99%
[29 empty] | 2019 | April | 3 | 12 | 29935 | 28500 | 105%
[29 empty] | 2019 | April | 3 | 13 | 7933.5 | 28500 | 27.84%
[29 empty] | 2019 | April | 3 | 14 | 9399.5 | 28500 | 32.98%
[29 empty] | 2019 | April | 3 | 15 | 1082 | 28500 | 3.796%
[29 empty] | 2019 | April | 3 | 16 | 10964.5 | 28500 | 38.47%
[29 empty] | 2019 | April | 3 | 17 | 6774 | 28500 | 23.77%
[29 empty] | 2019 | April | 3 | 18 | 148 | 28500 | 0.5193%
[29 empty] | 2019 | April | 3 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 3 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 3 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 3 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 3 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 4 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 4 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 4 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 4 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 4 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 4 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 4 | 6 | 536 | 28500 | 1.881%
[29 empty] | 2019 | April | 4 | 7 | 10027.5 | 28500 | 35.18%
[29 empty] | 2019 | April | 4 | 8 | 16045.5 | 28500 | 56.3%
[29 empty] | 2019 | April | 4 | 9 | 3801 | 28500 | 13.34%
[29 empty] | 2019 | April | 4 | 10 | 33847 | 28500 | 118.8%
[29 empty] | 2019 | April | 4 | 11 | 19507.5 | 28500 | 68.45%
[29 empty] | 2019 | April | 4 | 12 | 19220 | 28500 | 67.44%
[29 empty] | 2019 | April | 4 | 13 | 4795 | 28500 | 16.82%
[29 empty] | 2019 | April | 4 | 14 | 5316.5 | 28500 | 18.65%
[29 empty] | 2019 | April | 4 | 15 | 18563 | 28500 | 65.13%
[29 empty] | 2019 | April | 4 | 16 | 3263.5 | 28500 | 11.45%
[29 empty] | 2019 | April | 4 | 17 | 4749 | 28500 | 16.66%
[29 empty] | 2019 | April | 4 | 18 | 39.5 | 28500 | 0.1386%
[29 empty] | 2019 | April | 4 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 4 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 4 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 4 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 4 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 5 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 5 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 5 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 5 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 5 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 5 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 5 | 6 | 281.5 | 28500 | 0.9877%
[29 empty] | 2019 | April | 5 | 7 | 9713.5 | 28500 | 34.08%
[29 empty] | 2019 | April | 5 | 8 | 13116 | 28500 | 46.02%
[29 empty] | 2019 | April | 5 | 9 | 10960 | 28500 | 38.46%
[29 empty] | 2019 | April | 5 | 10 | 20014.5 | 28500 | 70.23%
[29 empty] | 2019 | April | 5 | 11 | 33524 | 28500 | 117.6%
[29 empty] | 2019 | April | 5 | 12 | 29831 | 28500 | 104.7%
[29 empty] | 2019 | April | 5 | 13 | 29253.5 | 28500 | 102.6%
[29 empty] | 2019 | April | 5 | 14 | 9575 | 28500 | 33.6%
[29 empty] | 2019 | April | 5 | 15 | 9789 | 28500 | 34.35%
[29 empty] | 2019 | April | 5 | 16 | 5421.5 | 28500 | 19.02%
[29 empty] | 2019 | April | 5 | 17 | 1744.5 | 28500 | 6.121%
[29 empty] | 2019 | April | 5 | 18 | 21 | 28500 | 0.07368%
[29 empty] | 2019 | April | 5 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 5 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 5 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 5 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 5 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 6 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 6 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 6 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 6 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 6 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 6 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 6 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 6 | 7 | 4884.5 | 28500 | 17.14%
[29 empty] | 2019 | April | 6 | 8 | 4246.5 | 28500 | 14.9%
[29 empty] | 2019 | April | 6 | 9 | 4624 | 28500 | 16.22%
[29 empty] | 2019 | April | 6 | 10 | 4015 | 28500 | 14.09%
[29 empty] | 2019 | April | 6 | 11 | 3070.5 | 28500 | 10.77%
[29 empty] | 2019 | April | 6 | 12 | 3413.5 | 28500 | 11.98%
[29 empty] | 2019 | April | 6 | 13 | 3025.5 | 28500 | 10.62%
[29 empty] | 2019 | April | 6 | 14 | 3026.5 | 28500 | 10.62%
[29 empty] | 2019 | April | 6 | 15 | 7353 | 28500 | 25.8%
[29 empty] | 2019 | April | 6 | 16 | 6178.5 | 28500 | 21.68%
[29 empty] | 2019 | April | 6 | 17 | 1074 | 28500 | 3.768%
[29 empty] | 2019 | April | 6 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 6 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 6 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 6 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 6 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 6 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 7 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 7 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 7 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 7 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 7 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 7 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 7 | 6 | 368.5 | 28500 | 1.293%
[29 empty] | 2019 | April | 7 | 7 | 2393 | 28500 | 8.396%
[29 empty] | 2019 | April | 7 | 8 | 3334.5 | 28500 | 11.7%
[29 empty] | 2019 | April | 7 | 9 | 5975 | 28500 | 20.96%
[29 empty] | 2019 | April | 7 | 10 | 6220.5 | 28500 | 21.83%
[29 empty] | 2019 | April | 7 | 11 | 5556.5 | 28500 | 19.5%
[29 empty] | 2019 | April | 7 | 12 | 4218.5 | 28500 | 14.8%
[29 empty] | 2019 | April | 7 | 13 | 4827.5 | 28500 | 16.94%
[29 empty] | 2019 | April | 7 | 14 | 4820 | 28500 | 16.91%
[29 empty] | 2019 | April | 7 | 15 | 12766 | 28500 | 44.79%
[29 empty] | 2019 | April | 7 | 16 | 6493 | 28500 | 22.78%
[29 empty] | 2019 | April | 7 | 17 | 3995.5 | 28500 | 14.02%
[29 empty] | 2019 | April | 7 | 18 | 20 | 28500 | 0.07018%
[29 empty] | 2019 | April | 7 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 7 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 7 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 7 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 7 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 8 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 8 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 8 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 8 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 8 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 8 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 8 | 6 | 1267 | 28500 | 4.446%
[29 empty] | 2019 | April | 8 | 7 | 4113.5 | 28500 | 14.43%
[29 empty] | 2019 | April | 8 | 8 | 7315.5 | 28500 | 25.67%
[29 empty] | 2019 | April | 8 | 9 | 3435 | 28500 | 12.05%
[29 empty] | 2019 | April | 8 | 10 | 16345.5 | 28500 | 57.35%
[29 empty] | 2019 | April | 8 | 11 | 14932 | 28500 | 52.39%
[29 empty] | 2019 | April | 8 | 12 | 18865 | 28500 | 66.19%
[29 empty] | 2019 | April | 8 | 13 | 29702.5 | 28500 | 104.2%
[29 empty] | 2019 | April | 8 | 14 | 25414 | 28500 | 89.17%
[29 empty] | 2019 | April | 8 | 15 | 20571.5 | 28500 | 72.18%
[29 empty] | 2019 | April | 8 | 16 | 16085.5 | 28500 | 56.44%
[29 empty] | 2019 | April | 8 | 17 | 4617.5 | 28500 | 16.2%
[29 empty] | 2019 | April | 8 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 8 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 8 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 8 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 8 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 8 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 9 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 9 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 9 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 9 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 9 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 9 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 9 | 6 | 222.5 | 28500 | 0.7807%
[29 empty] | 2019 | April | 9 | 7 | 1153 | 28500 | 4.046%
[29 empty] | 2019 | April | 9 | 8 | 3283.5 | 28500 | 11.52%
[29 empty] | 2019 | April | 9 | 9 | 2849.5 | 28500 | 9.998%
[29 empty] | 2019 | April | 9 | 10 | 2505.5 | 28500 | 8.791%
[29 empty] | 2019 | April | 9 | 11 | 2388 | 28500 | 8.379%
[29 empty] | 2019 | April | 9 | 12 | 7815 | 28500 | 27.42%
[29 empty] | 2019 | April | 9 | 13 | 5581 | 28500 | 19.58%
[29 empty] | 2019 | April | 9 | 14 | 11469 | 28500 | 40.24%
[29 empty] | 2019 | April | 9 | 15 | 8099.5 | 28500 | 28.42%
[29 empty] | 2019 | April | 9 | 16 | 5959.5 | 28500 | 20.91%
[29 empty] | 2019 | April | 9 | 17 | 3484.5 | 28500 | 12.23%
[29 empty] | 2019 | April | 9 | 18 | 5 | 28500 | 0.01754%
[29 empty] | 2019 | April | 9 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 9 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 9 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 9 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 9 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 10 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 10 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 10 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 10 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 10 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 10 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 10 | 6 | 589.5 | 28500 | 2.068%
[29 empty] | 2019 | April | 10 | 7 | 4868.5 | 28500 | 17.08%
[29 empty] | 2019 | April | 10 | 8 | 11696.5 | 28500 | 41.04%
[29 empty] | 2019 | April | 10 | 9 | 26068.5 | 28500 | 91.47%
[29 empty] | 2019 | April | 10 | 10 | 35313.5 | 28500 | 123.9%
[29 empty] | 2019 | April | 10 | 11 | 44556 | 28500 | 156.3%
[29 empty] | 2019 | April | 10 | 12 | 45241.5 | 28500 | 158.7%
[29 empty] | 2019 | April | 10 | 13 | 43138.5 | 28500 | 151.4%
[29 empty] | 2019 | April | 10 | 14 | 38512 | 28500 | 135.1%
[29 empty] | 2019 | April | 10 | 15 | 30947.5 | 28500 | 108.6%
[29 empty] | 2019 | April | 10 | 16 | 19987 | 28500 | 70.13%
[29 empty] | 2019 | April | 10 | 17 | 7592.5 | 28500 | 26.64%
[29 empty] | 2019 | April | 10 | 18 | 461 | 28500 | 1.618%
[29 empty] | 2019 | April | 10 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 10 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 10 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 10 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 10 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 11 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 11 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 11 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 11 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 11 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 11 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 11 | 6 | 1487 | 28500 | 5.218%
[29 empty] | 2019 | April | 11 | 7 | 10834 | 28500 | 38.01%
[29 empty] | 2019 | April | 11 | 8 | 19951.5 | 28500 | 70.01%
[29 empty] | 2019 | April | 11 | 9 | 23560.5 | 28500 | 82.67%
[29 empty] | 2019 | April | 11 | 10 | 16976.5 | 28500 | 59.57%
[29 empty] | 2019 | April | 11 | 11 | 23283.5 | 28500 | 81.7%
[29 empty] | 2019 | April | 11 | 12 | 32232.5 | 28500 | 113.1%
[29 empty] | 2019 | April | 11 | 13 | 37239.5 | 28500 | 130.7%
[29 empty] | 2019 | April | 11 | 14 | 35797.5 | 28500 | 125.6%
[29 empty] | 2019 | April | 11 | 15 | 30033 | 28500 | 105.4%
[29 empty] | 2019 | April | 11 | 16 | 19586 | 28500 | 68.72%
[29 empty] | 2019 | April | 11 | 17 | 7494 | 28500 | 26.29%
[29 empty] | 2019 | April | 11 | 18 | 516.5 | 28500 | 1.812%
[29 empty] | 2019 | April | 11 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 11 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 11 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 11 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 11 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 12 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 12 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 12 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 12 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 12 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 12 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 12 | 6 | 1716 | 28500 | 6.021%
[29 empty] | 2019 | April | 12 | 7 | 8074.5 | 28500 | 28.33%
[29 empty] | 2019 | April | 12 | 8 | 16154 | 28500 | 56.68%
[29 empty] | 2019 | April | 12 | 9 | 31543 | 28500 | 110.7%
[29 empty] | 2019 | April | 12 | 10 | 16602.5 | 28500 | 58.25%
[29 empty] | 2019 | April | 12 | 11 | 5479 | 28500 | 19.22%
[29 empty] | 2019 | April | 12 | 12 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 12 | 13 | 12490.5 | 28500 | 43.83%
[29 empty] | 2019 | April | 12 | 14 | 5460 | 28500 | 19.16%
[29 empty] | 2019 | April | 12 | 15 | 5375.5 | 28500 | 18.86%
[29 empty] | 2019 | April | 12 | 16 | 6476.5 | 28500 | 22.72%
[29 empty] | 2019 | April | 12 | 17 | 3131 | 28500 | 10.99%
[29 empty] | 2019 | April | 12 | 18 | 193 | 28500 | 0.6772%
[29 empty] | 2019 | April | 12 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 12 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 12 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 12 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 12 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 13 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 13 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 13 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 13 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 13 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 13 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 13 | 6 | 1746.5 | 28500 | 6.128%
[29 empty] | 2019 | April | 13 | 7 | 2976 | 28500 | 10.44%
[29 empty] | 2019 | April | 13 | 8 | 4226.5 | 28500 | 14.83%
[29 empty] | 2019 | April | 13 | 9 | 15108.5 | 28500 | 53.01%
[29 empty] | 2019 | April | 13 | 10 | 8393 | 28500 | 29.45%
[29 empty] | 2019 | April | 13 | 11 | 14106.5 | 28500 | 49.5%
[29 empty] | 2019 | April | 13 | 12 | 10328.5 | 28500 | 36.24%
[29 empty] | 2019 | April | 13 | 13 | 33977 | 28500 | 119.2%
[29 empty] | 2019 | April | 13 | 14 | 23998 | 28500 | 84.2%
[29 empty] | 2019 | April | 13 | 15 | 27711.5 | 28500 | 97.23%
[29 empty] | 2019 | April | 13 | 16 | 15805.5 | 28500 | 55.46%
[29 empty] | 2019 | April | 13 | 17 | 7155.5 | 28500 | 25.11%
[29 empty] | 2019 | April | 13 | 18 | 550.5 | 28500 | 1.932%
[29 empty] | 2019 | April | 13 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 13 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 13 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 13 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 13 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 14 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 14 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 14 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 14 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 14 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 14 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 14 | 6 | 1474.5 | 28500 | 5.174%
[29 empty] | 2019 | April | 14 | 7 | 3178.5 | 28500 | 11.15%
[29 empty] | 2019 | April | 14 | 8 | 23173.5 | 28500 | 81.31%
[29 empty] | 2019 | April | 14 | 9 | 25619 | 28500 | 89.89%
[29 empty] | 2019 | April | 14 | 10 | 25660 | 28500 | 90.04%
[29 empty] | 2019 | April | 14 | 11 | 24100 | 28500 | 84.56%
[29 empty] | 2019 | April | 14 | 12 | 24669.5 | 28500 | 86.56%
[29 empty] | 2019 | April | 14 | 13 | 25685.5 | 28500 | 90.12%
[29 empty] | 2019 | April | 14 | 14 | 15926.5 | 28500 | 55.88%
[29 empty] | 2019 | April | 14 | 15 | 21514.5 | 28500 | 75.49%
[29 empty] | 2019 | April | 14 | 16 | 12042 | 28500 | 42.25%
[29 empty] | 2019 | April | 14 | 17 | 5865 | 28500 | 20.58%
[29 empty] | 2019 | April | 14 | 18 | 729.5 | 28500 | 2.56%
[29 empty] | 2019 | April | 14 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 14 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 14 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 14 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 14 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 15 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 15 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 15 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 15 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 15 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 15 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 15 | 6 | 1742.5 | 28500 | 6.114%
[29 empty] | 2019 | April | 15 | 7 | 11403.5 | 28500 | 40.01%
[29 empty] | 2019 | April | 15 | 8 | 20101 | 28500 | 70.53%
[29 empty] | 2019 | April | 15 | 9 | 32491 | 28500 | 114%
[29 empty] | 2019 | April | 15 | 10 | 39212.5 | 28500 | 137.6%
[29 empty] | 2019 | April | 15 | 11 | 43266.5 | 28500 | 151.8%
[29 empty] | 2019 | April | 15 | 12 | 43837 | 28500 | 153.8%
[29 empty] | 2019 | April | 15 | 13 | 40175 | 28500 | 141%
[29 empty] | 2019 | April | 15 | 14 | 31597.5 | 28500 | 110.9%
[29 empty] | 2019 | April | 15 | 15 | 27416 | 28500 | 96.2%
[29 empty] | 2019 | April | 15 | 16 | 17412.5 | 28500 | 61.1%
[29 empty] | 2019 | April | 15 | 17 | 6825.5 | 28500 | 23.95%
[29 empty] | 2019 | April | 15 | 18 | 717 | 28500 | 2.516%
[29 empty] | 2019 | April | 15 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 15 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 15 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 15 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 15 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 16 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 16 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 16 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 16 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 16 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 16 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 16 | 6 | 615 | 28500 | 2.158%
[29 empty] | 2019 | April | 16 | 7 | 6876 | 28500 | 24.13%
[29 empty] | 2019 | April | 16 | 8 | 12717.5 | 28500 | 44.62%
[29 empty] | 2019 | April | 16 | 9 | 15138 | 28500 | 53.12%
[29 empty] | 2019 | April | 16 | 10 | 10551.5 | 28500 | 37.02%
[29 empty] | 2019 | April | 16 | 11 | 15655.5 | 28500 | 54.93%
[29 empty] | 2019 | April | 16 | 12 | 19756 | 28500 | 69.32%
[29 empty] | 2019 | April | 16 | 13 | 16779.5 | 28500 | 58.88%
[29 empty] | 2019 | April | 16 | 14 | 20704 | 28500 | 72.65%
[29 empty] | 2019 | April | 16 | 15 | 9994 | 28500 | 35.07%
[29 empty] | 2019 | April | 16 | 16 | 10784 | 28500 | 37.84%
[29 empty] | 2019 | April | 16 | 17 | 1192.5 | 28500 | 4.184%
[29 empty] | 2019 | April | 16 | 18 | 590 | 28500 | 2.07%
[29 empty] | 2019 | April | 16 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 16 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 16 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 16 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 16 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 17 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 17 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 17 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 17 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 17 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 17 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 17 | 6 | 2113 | 28500 | 7.414%
[29 empty] | 2019 | April | 17 | 7 | 11014 | 28500 | 38.65%
[29 empty] | 2019 | April | 17 | 8 | 19843 | 28500 | 69.62%
[29 empty] | 2019 | April | 17 | 9 | 29365.5 | 28500 | 103%
[29 empty] | 2019 | April | 17 | 10 | 34879 | 28500 | 122.4%
[29 empty] | 2019 | April | 17 | 11 | 37635.5 | 28500 | 132.1%
[29 empty] | 2019 | April | 17 | 12 | 36454.5 | 28500 | 127.9%
[29 empty] | 2019 | April | 17 | 13 | 22963.5 | 28500 | 80.57%
[29 empty] | 2019 | April | 17 | 14 | 23557 | 28500 | 82.66%
[29 empty] | 2019 | April | 17 | 15 | 17757.5 | 28500 | 62.31%
[29 empty] | 2019 | April | 17 | 16 | 13988 | 28500 | 49.08%
[29 empty] | 2019 | April | 17 | 17 | 6671.5 | 28500 | 23.41%
[29 empty] | 2019 | April | 17 | 18 | 793 | 28500 | 2.782%
[29 empty] | 2019 | April | 17 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 17 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 17 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 17 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 17 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 18 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 18 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 18 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 18 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 18 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 18 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 18 | 6 | 2100 | 28500 | 7.368%
[29 empty] | 2019 | April | 18 | 7 | 5503 | 28500 | 19.31%
[29 empty] | 2019 | April | 18 | 8 | 17951.5 | 28500 | 62.99%
[29 empty] | 2019 | April | 18 | 9 | 23333.5 | 28500 | 81.87%
[29 empty] | 2019 | April | 18 | 10 | 35684 | 28500 | 125.2%
[29 empty] | 2019 | April | 18 | 11 | 38870 | 28500 | 136.4%
[29 empty] | 2019 | April | 18 | 12 | 39826 | 28500 | 139.7%
[29 empty] | 2019 | April | 18 | 13 | 39689.5 | 28500 | 139.3%
[29 empty] | 2019 | April | 18 | 14 | 28534.5 | 28500 | 100.1%
[29 empty] | 2019 | April | 18 | 15 | 19714 | 28500 | 69.17%
[29 empty] | 2019 | April | 18 | 16 | 15602 | 28500 | 54.74%
[29 empty] | 2019 | April | 18 | 17 | 7360.5 | 28500 | 25.83%
[29 empty] | 2019 | April | 18 | 18 | 879.5 | 28500 | 3.086%
[29 empty] | 2019 | April | 18 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 18 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 18 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 18 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 18 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 19 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 19 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 19 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 19 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 19 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 19 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 19 | 6 | 2106 | 28500 | 7.389%
[29 empty] | 2019 | April | 19 | 7 | 11695.5 | 28500 | 41.04%
[29 empty] | 2019 | April | 19 | 8 | 22754.5 | 28500 | 79.84%
[29 empty] | 2019 | April | 19 | 9 | 30483.5 | 28500 | 107%
[29 empty] | 2019 | April | 19 | 10 | 37806.5 | 28500 | 132.7%
[29 empty] | 2019 | April | 19 | 11 | 41281 | 28500 | 144.8%
[29 empty] | 2019 | April | 19 | 12 | 41745.5 | 28500 | 146.5%
[29 empty] | 2019 | April | 19 | 13 | 39721.5 | 28500 | 139.4%
[29 empty] | 2019 | April | 19 | 14 | 35457.5 | 28500 | 124.4%
[29 empty] | 2019 | April | 19 | 15 | 28729.5 | 28500 | 100.8%
[29 empty] | 2019 | April | 19 | 16 | 18350.5 | 28500 | 64.39%
[29 empty] | 2019 | April | 19 | 17 | 7359 | 28500 | 25.82%
[29 empty] | 2019 | April | 19 | 18 | 752.5 | 28500 | 2.64%
[29 empty] | 2019 | April | 19 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 19 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 19 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 19 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 19 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 20 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 20 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 20 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 20 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 20 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 20 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 20 | 6 | 2382.5 | 28500 | 8.36%
[29 empty] | 2019 | April | 20 | 7 | 12503 | 28500 | 43.87%
[29 empty] | 2019 | April | 20 | 8 | 22865 | 28500 | 80.23%
[29 empty] | 2019 | April | 20 | 9 | 31977 | 28500 | 112.2%
[29 empty] | 2019 | April | 20 | 10 | 38213.5 | 28500 | 134.1%
[29 empty] | 2019 | April | 20 | 11 | 41571.5 | 28500 | 145.9%
[29 empty] | 2019 | April | 20 | 12 | 42239.5 | 28500 | 148.2%
[29 empty] | 2019 | April | 20 | 13 | 40247 | 28500 | 141.2%
[29 empty] | 2019 | April | 20 | 14 | 35310.5 | 28500 | 123.9%
[29 empty] | 2019 | April | 20 | 15 | 28593 | 28500 | 100.3%
[29 empty] | 2019 | April | 20 | 16 | 18325.5 | 28500 | 64.3%
[29 empty] | 2019 | April | 20 | 17 | 7378 | 28500 | 25.89%
[29 empty] | 2019 | April | 20 | 18 | 718.5 | 28500 | 2.521%
[29 empty] | 2019 | April | 20 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 20 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 20 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 20 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 20 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 21 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 21 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 21 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 21 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 21 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 21 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 21 | 6 | 2425 | 28500 | 8.509%
[29 empty] | 2019 | April | 21 | 7 | 12583 | 28500 | 44.15%
[29 empty] | 2019 | April | 21 | 8 | 22858.5 | 28500 | 80.21%
[29 empty] | 2019 | April | 21 | 9 | 31676 | 28500 | 111.1%
[29 empty] | 2019 | April | 21 | 10 | 37815 | 28500 | 132.7%
[29 empty] | 2019 | April | 21 | 11 | 40902 | 28500 | 143.5%
[29 empty] | 2019 | April | 21 | 12 | 41900.5 | 28500 | 147%
[29 empty] | 2019 | April | 21 | 13 | 39811.5 | 28500 | 139.7%
[29 empty] | 2019 | April | 21 | 14 | 34972 | 28500 | 122.7%
[29 empty] | 2019 | April | 21 | 15 | 27430.5 | 28500 | 96.25%
[29 empty] | 2019 | April | 21 | 16 | 18132 | 28500 | 63.62%
[29 empty] | 2019 | April | 21 | 17 | 7432.5 | 28500 | 26.08%
[29 empty] | 2019 | April | 21 | 18 | 870 | 28500 | 3.053%
[29 empty] | 2019 | April | 21 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 21 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 21 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 21 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 21 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 22 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 22 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 22 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 22 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 22 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 22 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 22 | 6 | 1706.5 | 28500 | 5.988%
[29 empty] | 2019 | April | 22 | 7 | 11235 | 28500 | 39.42%
[29 empty] | 2019 | April | 22 | 8 | 15943 | 28500 | 55.94%
[29 empty] | 2019 | April | 22 | 9 | 28521.5 | 28500 | 100.1%
[29 empty] | 2019 | April | 22 | 10 | 33470 | 28500 | 117.4%
[29 empty] | 2019 | April | 22 | 11 | 40181 | 28500 | 141%
[29 empty] | 2019 | April | 22 | 12 | 40850 | 28500 | 143.3%
[29 empty] | 2019 | April | 22 | 13 | 34846 | 28500 | 122.3%
[29 empty] | 2019 | April | 22 | 14 | 31591.5 | 28500 | 110.8%
[29 empty] | 2019 | April | 22 | 15 | 25785.5 | 28500 | 90.48%
[29 empty] | 2019 | April | 22 | 16 | 10396.5 | 28500 | 36.48%
[29 empty] | 2019 | April | 22 | 17 | 3299.5 | 28500 | 11.58%
[29 empty] | 2019 | April | 22 | 18 | 802 | 28500 | 2.814%
[29 empty] | 2019 | April | 22 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 22 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 22 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 22 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 22 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 23 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 23 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 23 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 23 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 23 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 23 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 23 | 6 | 2153.5 | 28500 | 7.556%
[29 empty] | 2019 | April | 23 | 7 | 7518 | 28500 | 26.38%
[29 empty] | 2019 | April | 23 | 8 | 10714 | 28500 | 37.59%
[29 empty] | 2019 | April | 23 | 9 | 16138 | 28500 | 56.62%
[29 empty] | 2019 | April | 23 | 10 | 18107.5 | 28500 | 63.54%
[29 empty] | 2019 | April | 23 | 11 | 24989.5 | 28500 | 87.68%
[29 empty] | 2019 | April | 23 | 12 | 22473 | 28500 | 78.85%
[29 empty] | 2019 | April | 23 | 13 | 18768 | 28500 | 65.85%
[29 empty] | 2019 | April | 23 | 14 | 13496.5 | 28500 | 47.36%
[29 empty] | 2019 | April | 23 | 15 | 13728 | 28500 | 48.17%
[29 empty] | 2019 | April | 23 | 16 | 1936 | 28500 | 6.793%
[29 empty] | 2019 | April | 23 | 17 | 3981 | 28500 | 13.97%
[29 empty] | 2019 | April | 23 | 18 | 1156.5 | 28500 | 4.058%
[29 empty] | 2019 | April | 23 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 23 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 23 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 23 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 23 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 24 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 24 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 24 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 24 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 24 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 24 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 24 | 6 | 2670 | 28500 | 9.368%
[29 empty] | 2019 | April | 24 | 7 | 10753.5 | 28500 | 37.73%
[29 empty] | 2019 | April | 24 | 8 | 13431.5 | 28500 | 47.13%
[29 empty] | 2019 | April | 24 | 9 | 11654.5 | 28500 | 40.89%
[29 empty] | 2019 | April | 24 | 10 | 2676 | 28500 | 9.389%
[29 empty] | 2019 | April | 24 | 11 | 3252.5 | 28500 | 11.41%
[29 empty] | 2019 | April | 24 | 12 | 20543 | 28500 | 72.08%
[29 empty] | 2019 | April | 24 | 13 | 11669 | 28500 | 40.94%
[29 empty] | 2019 | April | 24 | 14 | 10321.5 | 28500 | 36.22%
[29 empty] | 2019 | April | 24 | 15 | 23205.5 | 28500 | 81.42%
[29 empty] | 2019 | April | 24 | 16 | 15952.5 | 28500 | 55.97%
[29 empty] | 2019 | April | 24 | 17 | 7094 | 28500 | 24.89%
[29 empty] | 2019 | April | 24 | 18 | 1143 | 28500 | 4.011%
[29 empty] | 2019 | April | 24 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 24 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 24 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 24 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 24 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 25 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 25 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 25 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 25 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 25 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 25 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 25 | 6 | 3012 | 28500 | 10.57%
[29 empty] | 2019 | April | 25 | 7 | 4043 | 28500 | 14.19%
[29 empty] | 2019 | April | 25 | 8 | 12402 | 28500 | 43.52%
[29 empty] | 2019 | April | 25 | 9 | 8097.5 | 28500 | 28.41%
[29 empty] | 2019 | April | 25 | 10 | 24549.5 | 28500 | 86.14%
[29 empty] | 2019 | April | 25 | 11 | 25505 | 28500 | 89.49%
[29 empty] | 2019 | April | 25 | 12 | 26312.5 | 28500 | 92.32%
[29 empty] | 2019 | April | 25 | 13 | 31813 | 28500 | 111.6%
[29 empty] | 2019 | April | 25 | 14 | 24729 | 28500 | 86.77%
[29 empty] | 2019 | April | 25 | 15 | 13753 | 28500 | 48.26%
[29 empty] | 2019 | April | 25 | 16 | 18577.5 | 28500 | 65.18%
[29 empty] | 2019 | April | 25 | 17 | 7726.5 | 28500 | 27.11%
[29 empty] | 2019 | April | 25 | 18 | 889.5 | 28500 | 3.121%
[29 empty] | 2019 | April | 25 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 25 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 25 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 25 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 25 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 26 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 26 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 26 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 26 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 26 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 26 | 5 | 122.5 | 28500 | 0.4298%
[29 empty] | 2019 | April | 26 | 6 | 2738.5 | 28500 | 9.609%
[29 empty] | 2019 | April | 26 | 7 | 8700.5 | 28500 | 30.53%
[29 empty] | 2019 | April | 26 | 8 | 21294.5 | 28500 | 74.72%
[29 empty] | 2019 | April | 26 | 9 | 15931 | 28500 | 55.9%
[29 empty] | 2019 | April | 26 | 10 | 16497 | 28500 | 57.88%
[29 empty] | 2019 | April | 26 | 11 | 22522 | 28500 | 79.02%
[29 empty] | 2019 | April | 26 | 12 | 32686.5 | 28500 | 114.7%
[29 empty] | 2019 | April | 26 | 13 | 33424.5 | 28500 | 117.3%
[29 empty] | 2019 | April | 26 | 14 | 34718 | 28500 | 121.8%
[29 empty] | 2019 | April | 26 | 15 | 16102 | 28500 | 56.5%
[29 empty] | 2019 | April | 26 | 16 | 8737 | 28500 | 30.66%
[29 empty] | 2019 | April | 26 | 17 | 5268 | 28500 | 18.48%
[29 empty] | 2019 | April | 26 | 18 | 1377.5 | 28500 | 4.833%
[29 empty] | 2019 | April | 26 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 26 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 26 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 26 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 26 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 27 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 27 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 27 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 27 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 27 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 27 | 5 | 59 | 28500 | 0.207%
[29 empty] | 2019 | April | 27 | 6 | 457.5 | 28500 | 1.605%
[29 empty] | 2019 | April | 27 | 7 | 4913.5 | 28500 | 17.24%
[29 empty] | 2019 | April | 27 | 8 | 10314 | 28500 | 36.19%
[29 empty] | 2019 | April | 27 | 9 | 7231 | 28500 | 25.37%
[29 empty] | 2019 | April | 27 | 10 | 13120.5 | 28500 | 46.04%
[29 empty] | 2019 | April | 27 | 11 | 13062.5 | 28500 | 45.83%
[29 empty] | 2019 | April | 27 | 12 | 7692 | 28500 | 26.99%
[29 empty] | 2019 | April | 27 | 13 | 18144 | 28500 | 63.66%
[29 empty] | 2019 | April | 27 | 14 | 5187.5 | 28500 | 18.2%
[29 empty] | 2019 | April | 27 | 15 | 11761.5 | 28500 | 41.27%
[29 empty] | 2019 | April | 27 | 16 | 4596 | 28500 | 16.13%
[29 empty] | 2019 | April | 27 | 17 | 5686.5 | 28500 | 19.95%
[29 empty] | 2019 | April | 27 | 18 | 1127.5 | 28500 | 3.956%
[29 empty] | 2019 | April | 27 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 27 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 27 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 27 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 27 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 28 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 28 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 28 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 28 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 28 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 28 | 5 | 59.5 | 28500 | 0.2088%
[29 empty] | 2019 | April | 28 | 6 | 2258 | 28500 | 7.923%
[29 empty] | 2019 | April | 28 | 7 | 9153 | 28500 | 32.12%
[29 empty] | 2019 | April | 28 | 8 | 12170.5 | 28500 | 42.7%
[29 empty] | 2019 | April | 28 | 9 | 8972.5 | 28500 | 31.48%
[29 empty] | 2019 | April | 28 | 10 | 5068.5 | 28500 | 17.78%
[29 empty] | 2019 | April | 28 | 11 | 9608 | 28500 | 33.71%
[29 empty] | 2019 | April | 28 | 12 | 6380 | 28500 | 22.39%
[29 empty] | 2019 | April | 28 | 13 | 7932.5 | 28500 | 27.83%
[29 empty] | 2019 | April | 28 | 14 | 20415 | 28500 | 71.63%
[29 empty] | 2019 | April | 28 | 15 | 5100 | 28500 | 17.89%
[29 empty] | 2019 | April | 28 | 16 | 10832.5 | 28500 | 38.01%
[29 empty] | 2019 | April | 28 | 17 | 2393.5 | 28500 | 8.398%
[29 empty] | 2019 | April | 28 | 18 | 1050.5 | 28500 | 3.686%
[29 empty] | 2019 | April | 28 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 28 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 28 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 28 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 28 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 29 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 29 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 29 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 29 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 29 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 29 | 5 | 82 | 28500 | 0.2877%
[29 empty] | 2019 | April | 29 | 6 | 2762.5 | 28500 | 9.693%
[29 empty] | 2019 | April | 29 | 7 | 7425.5 | 28500 | 26.05%
[29 empty] | 2019 | April | 29 | 8 | 10333.5 | 28500 | 36.26%
[29 empty] | 2019 | April | 29 | 9 | 19653.5 | 28500 | 68.96%
[29 empty] | 2019 | April | 29 | 10 | 12275.5 | 28500 | 43.07%
[29 empty] | 2019 | April | 29 | 11 | 17023 | 28500 | 59.73%
[29 empty] | 2019 | April | 29 | 12 | 21065 | 28500 | 73.91%
[29 empty] | 2019 | April | 29 | 13 | 21974.5 | 28500 | 77.1%
[29 empty] | 2019 | April | 29 | 14 | 11726.5 | 28500 | 41.15%
[29 empty] | 2019 | April | 29 | 15 | 7596 | 28500 | 26.65%
[29 empty] | 2019 | April | 29 | 16 | 15190.5 | 28500 | 53.3%
[29 empty] | 2019 | April | 29 | 17 | 4545.5 | 28500 | 15.95%
[29 empty] | 2019 | April | 29 | 18 | 1503 | 28500 | 5.274%
[29 empty] | 2019 | April | 29 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 29 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 29 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 29 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 29 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 30 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 30 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 30 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 30 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 30 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 30 | 5 | 323.5 | 28500 | 1.135%
[29 empty] | 2019 | April | 30 | 6 | 3092 | 28500 | 10.85%
[29 empty] | 2019 | April | 30 | 7 | 7157 | 28500 | 25.11%
[29 empty] | 2019 | April | 30 | 8 | 10614 | 28500 | 37.24%
[29 empty] | 2019 | April | 30 | 9 | 20698.5 | 28500 | 72.63%
[29 empty] | 2019 | April | 30 | 10 | 25116.5 | 28500 | 88.13%
[29 empty] | 2019 | April | 30 | 11 | 28663 | 28500 | 100.6%
[29 empty] | 2019 | April | 30 | 12 | 34658 | 28500 | 121.6%
[29 empty] | 2019 | April | 30 | 13 | 31386.5 | 28500 | 110.1%
[29 empty] | 2019 | April | 30 | 14 | 30018.5 | 28500 | 105.3%
[29 empty] | 2019 | April | 30 | 15 | 24225.5 | 28500 | 85%
[29 empty] | 2019 | April | 30 | 16 | 16669.5 | 28500 | 58.49%
[29 empty] | 2019 | April | 30 | 17 | 7512.5 | 28500 | 26.36%
[29 empty] | 2019 | April | 30 | 18 | 1394 | 28500 | 4.891%
[29 empty] | 2019 | April | 30 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 30 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 30 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 30 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | April | 30 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 1 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 1 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 1 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 1 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 1 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 1 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 1 | 6 | 2564.5 | 28500 | 8.998%
[29 empty] | 2019 | May | 1 | 7 | 5321 | 28500 | 18.67%
[29 empty] | 2019 | May | 1 | 8 | 9357 | 28500 | 32.83%
[29 empty] | 2019 | May | 1 | 9 | 29711 | 28500 | 104.2%
[29 empty] | 2019 | May | 1 | 10 | 27312 | 28500 | 95.83%
[29 empty] | 2019 | May | 1 | 11 | 23230 | 28500 | 81.51%
[29 empty] | 2019 | May | 1 | 12 | 17209.5 | 28500 | 60.38%
[29 empty] | 2019 | May | 1 | 13 | 18090.5 | 28500 | 63.48%
[29 empty] | 2019 | May | 1 | 14 | 22626 | 28500 | 79.39%
[29 empty] | 2019 | May | 1 | 15 | 7309 | 28500 | 25.65%
[29 empty] | 2019 | May | 1 | 16 | 5521 | 28500 | 19.37%
[29 empty] | 2019 | May | 1 | 17 | 2619.5 | 28500 | 9.191%
[29 empty] | 2019 | May | 1 | 18 | 55 | 28500 | 0.193%
[29 empty] | 2019 | May | 1 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 1 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 1 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 1 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 1 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 2 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 2 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 2 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 2 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 2 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 2 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 2 | 6 | 3656 | 28500 | 12.83%
[29 empty] | 2019 | May | 2 | 7 | 13172.5 | 28500 | 46.22%
[29 empty] | 2019 | May | 2 | 8 | 22429 | 28500 | 78.7%
[29 empty] | 2019 | May | 2 | 9 | 28960 | 28500 | 101.6%
[29 empty] | 2019 | May | 2 | 10 | 23091 | 28500 | 81.02%
[29 empty] | 2019 | May | 2 | 11 | 9909 | 28500 | 34.77%
[29 empty] | 2019 | May | 2 | 12 | 5866.5 | 28500 | 20.58%
[29 empty] | 2019 | May | 2 | 13 | 22898 | 28500 | 80.34%
[29 empty] | 2019 | May | 2 | 14 | 12743.5 | 28500 | 44.71%
[29 empty] | 2019 | May | 2 | 15 | 4880 | 28500 | 17.12%
[29 empty] | 2019 | May | 2 | 16 | 4228 | 28500 | 14.84%
[29 empty] | 2019 | May | 2 | 17 | 1473.5 | 28500 | 5.17%
[29 empty] | 2019 | May | 2 | 18 | 118.5 | 28500 | 0.4158%
[29 empty] | 2019 | May | 2 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 2 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 2 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 2 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 2 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 3 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 3 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 3 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 3 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 3 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 3 | 5 | 436.5 | 28500 | 1.532%
[29 empty] | 2019 | May | 3 | 6 | 3784 | 28500 | 13.28%
[29 empty] | 2019 | May | 3 | 7 | 5194 | 28500 | 18.22%
[29 empty] | 2019 | May | 3 | 8 | 5080 | 28500 | 17.82%
[29 empty] | 2019 | May | 3 | 9 | 6434.5 | 28500 | 22.58%
[29 empty] | 2019 | May | 3 | 10 | 5025 | 28500 | 17.63%
[29 empty] | 2019 | May | 3 | 11 | 10587.5 | 28500 | 37.15%
[29 empty] | 2019 | May | 3 | 12 | 24051 | 28500 | 84.39%
[29 empty] | 2019 | May | 3 | 13 | 18569.5 | 28500 | 65.16%
[29 empty] | 2019 | May | 3 | 14 | 13620.5 | 28500 | 47.79%
[29 empty] | 2019 | May | 3 | 15 | 7874 | 28500 | 27.63%
[29 empty] | 2019 | May | 3 | 16 | 8280 | 28500 | 29.05%
[29 empty] | 2019 | May | 3 | 17 | 4250 | 28500 | 14.91%
[29 empty] | 2019 | May | 3 | 18 | 622 | 28500 | 2.182%
[29 empty] | 2019 | May | 3 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 3 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 3 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 3 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 3 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 4 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 4 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 4 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 4 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 4 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 4 | 5 | 382 | 28500 | 1.34%
[29 empty] | 2019 | May | 4 | 6 | 3776 | 28500 | 13.25%
[29 empty] | 2019 | May | 4 | 7 | 14560 | 28500 | 51.09%
[29 empty] | 2019 | May | 4 | 8 | 22891 | 28500 | 80.32%
[29 empty] | 2019 | May | 4 | 9 | 26519 | 28500 | 93.05%
[29 empty] | 2019 | May | 4 | 10 | 35592.5 | 28500 | 124.9%
[29 empty] | 2019 | May | 4 | 11 | 35364.5 | 28500 | 124.1%
[29 empty] | 2019 | May | 4 | 12 | 18985 | 28500 | 66.61%
[29 empty] | 2019 | May | 4 | 13 | 35803.5 | 28500 | 125.6%
[29 empty] | 2019 | May | 4 | 14 | 29458 | 28500 | 103.4%
[29 empty] | 2019 | May | 4 | 15 | 14534.5 | 28500 | 51%
[29 empty] | 2019 | May | 4 | 16 | 18938 | 28500 | 66.45%
[29 empty] | 2019 | May | 4 | 17 | 6967 | 28500 | 24.45%
[29 empty] | 2019 | May | 4 | 18 | 1370.5 | 28500 | 4.809%
[29 empty] | 2019 | May | 4 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 4 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 4 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 4 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 4 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 5 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 5 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 5 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 5 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 5 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 5 | 5 | 620.5 | 28500 | 2.177%
[29 empty] | 2019 | May | 5 | 6 | 3514.5 | 28500 | 12.33%
[29 empty] | 2019 | May | 5 | 7 | 14556.5 | 28500 | 51.08%
[29 empty] | 2019 | May | 5 | 8 | 25326 | 28500 | 88.86%
[29 empty] | 2019 | May | 5 | 9 | 24840.5 | 28500 | 87.16%
[29 empty] | 2019 | May | 5 | 10 | 21896 | 28500 | 76.83%
[29 empty] | 2019 | May | 5 | 11 | 14200 | 28500 | 49.82%
[29 empty] | 2019 | May | 5 | 12 | 17883.5 | 28500 | 62.75%
[29 empty] | 2019 | May | 5 | 13 | 13452 | 28500 | 47.2%
[29 empty] | 2019 | May | 5 | 14 | 7215 | 28500 | 25.32%
[29 empty] | 2019 | May | 5 | 15 | 13435.5 | 28500 | 47.14%
[29 empty] | 2019 | May | 5 | 16 | 13129.5 | 28500 | 46.07%
[29 empty] | 2019 | May | 5 | 17 | 8168 | 28500 | 28.66%
[29 empty] | 2019 | May | 5 | 18 | 1415.5 | 28500 | 4.967%
[29 empty] | 2019 | May | 5 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 5 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 5 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 5 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 5 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 6 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 6 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 6 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 6 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 6 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 6 | 5 | 705.5 | 28500 | 2.475%
[29 empty] | 2019 | May | 6 | 6 | 3270 | 28500 | 11.47%
[29 empty] | 2019 | May | 6 | 7 | 12700.5 | 28500 | 44.56%
[29 empty] | 2019 | May | 6 | 8 | 17556.5 | 28500 | 61.6%
[29 empty] | 2019 | May | 6 | 9 | 13940 | 28500 | 48.91%
[29 empty] | 2019 | May | 6 | 10 | 10373 | 28500 | 36.4%
[29 empty] | 2019 | May | 6 | 11 | 14342 | 28500 | 50.32%
[29 empty] | 2019 | May | 6 | 12 | 14166 | 28500 | 49.71%
[29 empty] | 2019 | May | 6 | 13 | 10154 | 28500 | 35.63%
[29 empty] | 2019 | May | 6 | 14 | 14345 | 28500 | 50.33%
[29 empty] | 2019 | May | 6 | 15 | 17941 | 28500 | 62.95%
[29 empty] | 2019 | May | 6 | 16 | 12191 | 28500 | 42.78%
[29 empty] | 2019 | May | 6 | 17 | 5792.5 | 28500 | 20.32%
[29 empty] | 2019 | May | 6 | 18 | 1985 | 28500 | 6.965%
[29 empty] | 2019 | May | 6 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 6 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 6 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 6 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 6 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 7 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 7 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 7 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 7 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 7 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 7 | 5 | 800.5 | 28500 | 2.809%
[29 empty] | 2019 | May | 7 | 6 | 3992.5 | 28500 | 14.01%
[29 empty] | 2019 | May | 7 | 7 | 11776 | 28500 | 41.32%
[29 empty] | 2019 | May | 7 | 8 | 21783 | 28500 | 76.43%
[29 empty] | 2019 | May | 7 | 9 | 30505 | 28500 | 107%
[29 empty] | 2019 | May | 7 | 10 | 30330.5 | 28500 | 106.4%
[29 empty] | 2019 | May | 7 | 11 | 26606 | 28500 | 93.35%
[29 empty] | 2019 | May | 7 | 12 | 26540.5 | 28500 | 93.12%
[29 empty] | 2019 | May | 7 | 13 | 16688 | 28500 | 58.55%
[29 empty] | 2019 | May | 7 | 14 | 15600.5 | 28500 | 54.74%
[29 empty] | 2019 | May | 7 | 15 | 22218.5 | 28500 | 77.96%
[29 empty] | 2019 | May | 7 | 16 | 12425 | 28500 | 43.6%
[29 empty] | 2019 | May | 7 | 17 | 6898 | 28500 | 24.2%
[29 empty] | 2019 | May | 7 | 18 | 1903 | 28500 | 6.677%
[29 empty] | 2019 | May | 7 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 7 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 7 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 7 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 7 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 8 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 8 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 8 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 8 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 8 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 8 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 8 | 6 | 4069.5 | 28500 | 14.28%
[29 empty] | 2019 | May | 8 | 7 | 5493.5 | 28500 | 19.28%
[29 empty] | 2019 | May | 8 | 8 | 1833 | 28500 | 6.432%
[29 empty] | 2019 | May | 8 | 9 | 3775.5 | 28500 | 13.25%
[29 empty] | 2019 | May | 8 | 10 | 3252 | 28500 | 11.41%
[29 empty] | 2019 | May | 8 | 11 | 7231 | 28500 | 25.37%
[29 empty] | 2019 | May | 8 | 12 | 22706 | 28500 | 79.67%
[29 empty] | 2019 | May | 8 | 13 | 31996.5 | 28500 | 112.3%
[29 empty] | 2019 | May | 8 | 14 | 25947 | 28500 | 91.04%
[29 empty] | 2019 | May | 8 | 15 | 23936 | 28500 | 83.99%
[29 empty] | 2019 | May | 8 | 16 | 16092 | 28500 | 56.46%
[29 empty] | 2019 | May | 8 | 17 | 7113.5 | 28500 | 24.96%
[29 empty] | 2019 | May | 8 | 18 | 984 | 28500 | 3.453%
[29 empty] | 2019 | May | 8 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 8 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 8 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 8 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 8 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 9 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 9 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 9 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 9 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 9 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 9 | 5 | 791 | 28500 | 2.775%
[29 empty] | 2019 | May | 9 | 6 | 3394 | 28500 | 11.91%
[29 empty] | 2019 | May | 9 | 7 | 13611.5 | 28500 | 47.76%
[29 empty] | 2019 | May | 9 | 8 | 17539.5 | 28500 | 61.54%
[29 empty] | 2019 | May | 9 | 9 | 19596.5 | 28500 | 68.76%
[29 empty] | 2019 | May | 9 | 10 | 16424.5 | 28500 | 57.63%
[29 empty] | 2019 | May | 9 | 11 | 34346.5 | 28500 | 120.5%
[29 empty] | 2019 | May | 9 | 12 | 4727 | 28500 | 16.59%
[29 empty] | 2019 | May | 9 | 13 | 2489.5 | 28500 | 8.735%
[29 empty] | 2019 | May | 9 | 14 | 6295.5 | 28500 | 22.09%
[29 empty] | 2019 | May | 9 | 15 | 6451.5 | 28500 | 22.64%
[29 empty] | 2019 | May | 9 | 16 | 3022 | 28500 | 10.6%
[29 empty] | 2019 | May | 9 | 17 | 2810.5 | 28500 | 9.861%
[29 empty] | 2019 | May | 9 | 18 | 119 | 28500 | 0.4175%
[29 empty] | 2019 | May | 9 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 9 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 9 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 9 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 9 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 10 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 10 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 10 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 10 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 10 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 10 | 5 | 194 | 28500 | 0.6807%
[29 empty] | 2019 | May | 10 | 6 | 3759.5 | 28500 | 13.19%
[29 empty] | 2019 | May | 10 | 7 | 6222 | 28500 | 21.83%
[29 empty] | 2019 | May | 10 | 8 | 12014 | 28500 | 42.15%
[29 empty] | 2019 | May | 10 | 9 | 26048 | 28500 | 91.4%
[29 empty] | 2019 | May | 10 | 10 | 22922.5 | 28500 | 80.43%
[29 empty] | 2019 | May | 10 | 11 | 26300.5 | 28500 | 92.28%
[29 empty] | 2019 | May | 10 | 12 | 9439 | 28500 | 33.12%
[29 empty] | 2019 | May | 10 | 13 | 9894.5 | 28500 | 34.72%
[29 empty] | 2019 | May | 10 | 14 | 28987.5 | 28500 | 101.7%
[29 empty] | 2019 | May | 10 | 15 | 27034.5 | 28500 | 94.86%
[29 empty] | 2019 | May | 10 | 16 | 15114 | 28500 | 53.03%
[29 empty] | 2019 | May | 10 | 17 | 7176 | 28500 | 25.18%
[29 empty] | 2019 | May | 10 | 18 | 1504 | 28500 | 5.277%
[29 empty] | 2019 | May | 10 | 19 | 20.5 | 28500 | 0.07193%
[29 empty] | 2019 | May | 10 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 10 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 10 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 10 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 11 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 11 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 11 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 11 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 11 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 11 | 5 | 674 | 28500 | 2.365%
[29 empty] | 2019 | May | 11 | 6 | 4004.5 | 28500 | 14.05%
[29 empty] | 2019 | May | 11 | 7 | 2473 | 28500 | 8.677%
[29 empty] | 2019 | May | 11 | 8 | 2915 | 28500 | 10.23%
[29 empty] | 2019 | May | 11 | 9 | 3901.5 | 28500 | 13.69%
[29 empty] | 2019 | May | 11 | 10 | 16118 | 28500 | 56.55%
[29 empty] | 2019 | May | 11 | 11 | 19731.5 | 28500 | 69.23%
[29 empty] | 2019 | May | 11 | 12 | 8731.5 | 28500 | 30.64%
[29 empty] | 2019 | May | 11 | 13 | 23509 | 28500 | 82.49%
[29 empty] | 2019 | May | 11 | 14 | 23520 | 28500 | 82.53%
[29 empty] | 2019 | May | 11 | 15 | 11240.5 | 28500 | 39.44%
[29 empty] | 2019 | May | 11 | 16 | 13791 | 28500 | 48.39%
[29 empty] | 2019 | May | 11 | 17 | 8364 | 28500 | 29.35%
[29 empty] | 2019 | May | 11 | 18 | 1672.5 | 28500 | 5.868%
[29 empty] | 2019 | May | 11 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 11 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 11 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 11 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 11 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 12 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 12 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 12 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 12 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 12 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 12 | 5 | 1089.5 | 28500 | 3.823%
[29 empty] | 2019 | May | 12 | 6 | 3655 | 28500 | 12.82%
[29 empty] | 2019 | May | 12 | 7 | 14102 | 28500 | 49.48%
[29 empty] | 2019 | May | 12 | 8 | 24566.5 | 28500 | 86.2%
[29 empty] | 2019 | May | 12 | 9 | 33538.5 | 28500 | 117.7%
[29 empty] | 2019 | May | 12 | 10 | 38412 | 28500 | 134.8%
[29 empty] | 2019 | May | 12 | 11 | 41201.5 | 28500 | 144.6%
[29 empty] | 2019 | May | 12 | 12 | 37018.5 | 28500 | 129.9%
[29 empty] | 2019 | May | 12 | 13 | 27179 | 28500 | 95.36%
[29 empty] | 2019 | May | 12 | 14 | 23441.5 | 28500 | 82.25%
[29 empty] | 2019 | May | 12 | 15 | 19951 | 28500 | 70%
[29 empty] | 2019 | May | 12 | 16 | 19231 | 28500 | 67.48%
[29 empty] | 2019 | May | 12 | 17 | 8296 | 28500 | 29.11%
[29 empty] | 2019 | May | 12 | 18 | 1059 | 28500 | 3.716%
[29 empty] | 2019 | May | 12 | 19 | 57 | 28500 | 0.2%
[29 empty] | 2019 | May | 12 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 12 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 12 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 12 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 13 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 13 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 13 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 13 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 13 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 13 | 5 | 998.5 | 28500 | 3.504%
[29 empty] | 2019 | May | 13 | 6 | 3723.5 | 28500 | 13.06%
[29 empty] | 2019 | May | 13 | 7 | 14153 | 28500 | 49.66%
[29 empty] | 2019 | May | 13 | 8 | 21662 | 28500 | 76.01%
[29 empty] | 2019 | May | 13 | 9 | 32302.5 | 28500 | 113.3%
[29 empty] | 2019 | May | 13 | 10 | 39168.5 | 28500 | 137.4%
[29 empty] | 2019 | May | 13 | 11 | 42280.5 | 28500 | 148.4%
[29 empty] | 2019 | May | 13 | 12 | 43132 | 28500 | 151.3%
[29 empty] | 2019 | May | 13 | 13 | 41294.5 | 28500 | 144.9%
[29 empty] | 2019 | May | 13 | 14 | 35974 | 28500 | 126.2%
[29 empty] | 2019 | May | 13 | 15 | 28670.5 | 28500 | 100.6%
[29 empty] | 2019 | May | 13 | 16 | 19715 | 28500 | 69.18%
[29 empty] | 2019 | May | 13 | 17 | 6334.5 | 28500 | 22.23%
[29 empty] | 2019 | May | 13 | 18 | 2313.5 | 28500 | 8.118%
[29 empty] | 2019 | May | 13 | 19 | 98 | 28500 | 0.3439%
[29 empty] | 2019 | May | 13 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 13 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 13 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 13 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 14 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 14 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 14 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 14 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 14 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 14 | 5 | 1048.5 | 28500 | 3.679%
[29 empty] | 2019 | May | 14 | 6 | 3857.5 | 28500 | 13.54%
[29 empty] | 2019 | May | 14 | 7 | 14196 | 28500 | 49.81%
[29 empty] | 2019 | May | 14 | 8 | 24721 | 28500 | 86.74%
[29 empty] | 2019 | May | 14 | 9 | 33179.5 | 28500 | 116.4%
[29 empty] | 2019 | May | 14 | 10 | 38763 | 28500 | 136%
[29 empty] | 2019 | May | 14 | 11 | 42321.5 | 28500 | 148.5%
[29 empty] | 2019 | May | 14 | 12 | 43000 | 28500 | 150.9%
[29 empty] | 2019 | May | 14 | 13 | 40955.5 | 28500 | 143.7%
[29 empty] | 2019 | May | 14 | 14 | 35720.5 | 28500 | 125.3%
[29 empty] | 2019 | May | 14 | 15 | 28817 | 28500 | 101.1%
[29 empty] | 2019 | May | 14 | 16 | 19399.5 | 28500 | 68.07%
[29 empty] | 2019 | May | 14 | 17 | 8514.5 | 28500 | 29.88%
[29 empty] | 2019 | May | 14 | 18 | 958 | 28500 | 3.361%
[29 empty] | 2019 | May | 14 | 19 | 119 | 28500 | 0.4175%
[29 empty] | 2019 | May | 14 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 14 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 14 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 14 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 15 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 15 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 15 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 15 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 15 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 15 | 5 | 1209 | 28500 | 4.242%
[29 empty] | 2019 | May | 15 | 6 | 4279 | 28500 | 15.01%
[29 empty] | 2019 | May | 15 | 7 | 13911 | 28500 | 48.81%
[29 empty] | 2019 | May | 15 | 8 | 24005 | 28500 | 84.23%
[29 empty] | 2019 | May | 15 | 9 | 32083 | 28500 | 112.6%
[29 empty] | 2019 | May | 15 | 10 | 36389.5 | 28500 | 127.7%
[29 empty] | 2019 | May | 15 | 11 | 39573 | 28500 | 138.9%
[29 empty] | 2019 | May | 15 | 12 | 40046 | 28500 | 140.5%
[29 empty] | 2019 | May | 15 | 13 | 38281.5 | 28500 | 134.3%
[29 empty] | 2019 | May | 15 | 14 | 32813 | 28500 | 115.1%
[29 empty] | 2019 | May | 15 | 15 | 25780.5 | 28500 | 90.46%
[29 empty] | 2019 | May | 15 | 16 | 16159 | 28500 | 56.7%
[29 empty] | 2019 | May | 15 | 17 | 8176 | 28500 | 28.69%
[29 empty] | 2019 | May | 15 | 18 | 977 | 28500 | 3.428%
[29 empty] | 2019 | May | 15 | 19 | 4 | 28500 | 0.01404%
[29 empty] | 2019 | May | 15 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 15 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 15 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 15 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 16 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 16 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 16 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 16 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 16 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 16 | 5 | 1273.5 | 28500 | 4.468%
[29 empty] | 2019 | May | 16 | 6 | 4061 | 28500 | 14.25%
[29 empty] | 2019 | May | 16 | 7 | 13672.5 | 28500 | 47.97%
[29 empty] | 2019 | May | 16 | 8 | 24319 | 28500 | 85.33%
[29 empty] | 2019 | May | 16 | 9 | 30941.5 | 28500 | 108.6%
[29 empty] | 2019 | May | 16 | 10 | 35528.5 | 28500 | 124.7%
[29 empty] | 2019 | May | 16 | 11 | 33575 | 28500 | 117.8%
[29 empty] | 2019 | May | 16 | 12 | 39323 | 28500 | 138%
[29 empty] | 2019 | May | 16 | 13 | 41259.5 | 28500 | 144.8%
[29 empty] | 2019 | May | 16 | 14 | 36215.5 | 28500 | 127.1%
[29 empty] | 2019 | May | 16 | 15 | 29353 | 28500 | 103%
[29 empty] | 2019 | May | 16 | 16 | 19800.5 | 28500 | 69.48%
[29 empty] | 2019 | May | 16 | 17 | 8688.5 | 28500 | 30.49%
[29 empty] | 2019 | May | 16 | 18 | 1111 | 28500 | 3.898%
[29 empty] | 2019 | May | 16 | 19 | 164 | 28500 | 0.5754%
[29 empty] | 2019 | May | 16 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 16 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 16 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 16 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 17 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 17 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 17 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 17 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 17 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 17 | 5 | 454.5 | 28500 | 1.595%
[29 empty] | 2019 | May | 17 | 6 | 702 | 28500 | 2.463%
[29 empty] | 2019 | May | 17 | 7 | 3726.5 | 28500 | 13.08%
[29 empty] | 2019 | May | 17 | 8 | 5566.5 | 28500 | 19.53%
[29 empty] | 2019 | May | 17 | 9 | 2628.5 | 28500 | 9.223%
[29 empty] | 2019 | May | 17 | 10 | 4621 | 28500 | 16.21%
[29 empty] | 2019 | May | 17 | 11 | 8075.5 | 28500 | 28.34%
[29 empty] | 2019 | May | 17 | 12 | 3444.5 | 28500 | 12.09%
[29 empty] | 2019 | May | 17 | 13 | 3858.5 | 28500 | 13.54%
[29 empty] | 2019 | May | 17 | 14 | 3022.5 | 28500 | 10.61%
[29 empty] | 2019 | May | 17 | 15 | 4289.5 | 28500 | 15.05%
[29 empty] | 2019 | May | 17 | 16 | 2987 | 28500 | 10.48%
[29 empty] | 2019 | May | 17 | 17 | 1652.5 | 28500 | 5.798%
[29 empty] | 2019 | May | 17 | 18 | 691.5 | 28500 | 2.426%
[29 empty] | 2019 | May | 17 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 17 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 17 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 17 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 17 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 18 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 18 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 18 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 18 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 18 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 18 | 5 | 1128 | 28500 | 3.958%
[29 empty] | 2019 | May | 18 | 6 | 4615 | 28500 | 16.19%
[29 empty] | 2019 | May | 18 | 7 | 8733.5 | 28500 | 30.64%
[29 empty] | 2019 | May | 18 | 8 | 15818 | 28500 | 55.5%
[29 empty] | 2019 | May | 18 | 9 | 10689.5 | 28500 | 37.51%
[29 empty] | 2019 | May | 18 | 10 | 3908 | 28500 | 13.71%
[29 empty] | 2019 | May | 18 | 11 | 7398 | 28500 | 25.96%
[29 empty] | 2019 | May | 18 | 12 | 17301 | 28500 | 60.71%
[29 empty] | 2019 | May | 18 | 13 | 17754.5 | 28500 | 62.3%
[29 empty] | 2019 | May | 18 | 14 | 3447.5 | 28500 | 12.1%
[29 empty] | 2019 | May | 18 | 15 | 8191.5 | 28500 | 28.74%
[29 empty] | 2019 | May | 18 | 16 | 3004 | 28500 | 10.54%
[29 empty] | 2019 | May | 18 | 17 | 5194 | 28500 | 18.22%
[29 empty] | 2019 | May | 18 | 18 | 616.5 | 28500 | 2.163%
[29 empty] | 2019 | May | 18 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 18 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 18 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 18 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 18 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 19 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 19 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 19 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 19 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 19 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 19 | 5 | 749.5 | 28500 | 2.63%
[29 empty] | 2019 | May | 19 | 6 | 1998.5 | 28500 | 7.012%
[29 empty] | 2019 | May | 19 | 7 | 8739 | 28500 | 30.66%
[29 empty] | 2019 | May | 19 | 8 | 9317 | 28500 | 32.69%
[29 empty] | 2019 | May | 19 | 9 | 11600 | 28500 | 40.7%
[29 empty] | 2019 | May | 19 | 10 | 14495 | 28500 | 50.86%
[29 empty] | 2019 | May | 19 | 11 | 19475 | 28500 | 68.33%
[29 empty] | 2019 | May | 19 | 12 | 20656 | 28500 | 72.48%
[29 empty] | 2019 | May | 19 | 13 | 27849.5 | 28500 | 97.72%
[29 empty] | 2019 | May | 19 | 14 | 19988 | 28500 | 70.13%
[29 empty] | 2019 | May | 19 | 15 | 12417 | 28500 | 43.57%
[29 empty] | 2019 | May | 19 | 16 | 8350 | 28500 | 29.3%
[29 empty] | 2019 | May | 19 | 17 | 7172.5 | 28500 | 25.17%
[29 empty] | 2019 | May | 19 | 18 | 1655 | 28500 | 5.807%
[29 empty] | 2019 | May | 19 | 19 | 3.5 | 28500 | 0.01228%
[29 empty] | 2019 | May | 19 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 19 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 19 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 19 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 20 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 20 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 20 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 20 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 20 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 20 | 5 | 1426.5 | 28500 | 5.005%
[29 empty] | 2019 | May | 20 | 6 | 4046.5 | 28500 | 14.2%
[29 empty] | 2019 | May | 20 | 7 | 8341 | 28500 | 29.27%
[29 empty] | 2019 | May | 20 | 8 | 20590 | 28500 | 72.25%
[29 empty] | 2019 | May | 20 | 9 | 19302 | 28500 | 67.73%
[29 empty] | 2019 | May | 20 | 10 | 22688 | 28500 | 79.61%
[29 empty] | 2019 | May | 20 | 11 | 16186 | 28500 | 56.79%
[29 empty] | 2019 | May | 20 | 12 | 9891 | 28500 | 34.71%
[29 empty] | 2019 | May | 20 | 13 | 7336 | 28500 | 25.74%
[29 empty] | 2019 | May | 20 | 14 | 9234 | 28500 | 32.4%
[29 empty] | 2019 | May | 20 | 15 | 21757.5 | 28500 | 76.34%
[29 empty] | 2019 | May | 20 | 16 | 11513.5 | 28500 | 40.4%
[29 empty] | 2019 | May | 20 | 17 | 2735 | 28500 | 9.596%
[29 empty] | 2019 | May | 20 | 18 | 2442.5 | 28500 | 8.57%
[29 empty] | 2019 | May | 20 | 19 | 93.5 | 28500 | 0.3281%
[29 empty] | 2019 | May | 20 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 20 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 20 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 20 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 21 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 21 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 21 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 21 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 21 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 21 | 5 | 1264.5 | 28500 | 4.437%
[29 empty] | 2019 | May | 21 | 6 | 4387.5 | 28500 | 15.39%
[29 empty] | 2019 | May | 21 | 7 | 14270 | 28500 | 50.07%
[29 empty] | 2019 | May | 21 | 8 | 24132 | 28500 | 84.67%
[29 empty] | 2019 | May | 21 | 9 | 32417.5 | 28500 | 113.7%
[29 empty] | 2019 | May | 21 | 10 | 37937.5 | 28500 | 133.1%
[29 empty] | 2019 | May | 21 | 11 | 41003.5 | 28500 | 143.9%
[29 empty] | 2019 | May | 21 | 12 | 39744 | 28500 | 139.5%
[29 empty] | 2019 | May | 21 | 13 | 29401.5 | 28500 | 103.2%
[29 empty] | 2019 | May | 21 | 14 | 24783.5 | 28500 | 86.96%
[29 empty] | 2019 | May | 21 | 15 | 16856.5 | 28500 | 59.15%
[29 empty] | 2019 | May | 21 | 16 | 12554 | 28500 | 44.05%
[29 empty] | 2019 | May | 21 | 17 | 7157 | 28500 | 25.11%
[29 empty] | 2019 | May | 21 | 18 | 2768 | 28500 | 9.712%
[29 empty] | 2019 | May | 21 | 19 | 181.5 | 28500 | 0.6368%
[29 empty] | 2019 | May | 21 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 21 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 21 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 21 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 22 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 22 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 22 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 22 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 22 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 22 | 5 | 214.5 | 28500 | 0.7526%
[29 empty] | 2019 | May | 22 | 6 | 3849.5 | 28500 | 13.51%
[29 empty] | 2019 | May | 22 | 7 | 7380 | 28500 | 25.89%
[29 empty] | 2019 | May | 22 | 8 | 20916.5 | 28500 | 73.39%
[29 empty] | 2019 | May | 22 | 9 | 26666 | 28500 | 93.56%
[29 empty] | 2019 | May | 22 | 10 | 30253.5 | 28500 | 106.2%
[29 empty] | 2019 | May | 22 | 11 | 29175 | 28500 | 102.4%
[29 empty] | 2019 | May | 22 | 12 | 22103.5 | 28500 | 77.56%
[29 empty] | 2019 | May | 22 | 13 | 19654 | 28500 | 68.96%
[29 empty] | 2019 | May | 22 | 14 | 30762.5 | 28500 | 107.9%
[29 empty] | 2019 | May | 22 | 15 | 26867.5 | 28500 | 94.27%
[29 empty] | 2019 | May | 22 | 16 | 18891.5 | 28500 | 66.29%
[29 empty] | 2019 | May | 22 | 17 | 8545 | 28500 | 29.98%
[29 empty] | 2019 | May | 22 | 18 | 1513.5 | 28500 | 5.311%
[29 empty] | 2019 | May | 22 | 19 | 410.5 | 28500 | 1.44%
[29 empty] | 2019 | May | 22 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 22 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 22 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 22 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 23 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 23 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 23 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 23 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 23 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 23 | 5 | 1033.5 | 28500 | 3.626%
[29 empty] | 2019 | May | 23 | 6 | 3792 | 28500 | 13.31%
[29 empty] | 2019 | May | 23 | 7 | 13463 | 28500 | 47.24%
[29 empty] | 2019 | May | 23 | 8 | 18974.5 | 28500 | 66.58%
[29 empty] | 2019 | May | 23 | 9 | 29910.5 | 28500 | 104.9%
[29 empty] | 2019 | May | 23 | 10 | 36701.5 | 28500 | 128.8%
[29 empty] | 2019 | May | 23 | 11 | 39254 | 28500 | 137.7%
[29 empty] | 2019 | May | 23 | 12 | 36196.5 | 28500 | 127%
[29 empty] | 2019 | May | 23 | 13 | 34743 | 28500 | 121.9%
[29 empty] | 2019 | May | 23 | 14 | 30325 | 28500 | 106.4%
[29 empty] | 2019 | May | 23 | 15 | 26422.5 | 28500 | 92.71%
[29 empty] | 2019 | May | 23 | 16 | 14497 | 28500 | 50.87%
[29 empty] | 2019 | May | 23 | 17 | 8507.5 | 28500 | 29.85%
[29 empty] | 2019 | May | 23 | 18 | 1457.5 | 28500 | 5.114%
[29 empty] | 2019 | May | 23 | 19 | 228 | 28500 | 0.8%
[29 empty] | 2019 | May | 23 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 23 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 23 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 23 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 24 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 24 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 24 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 24 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 24 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 24 | 5 | 1187.5 | 28500 | 4.167%
[29 empty] | 2019 | May | 24 | 6 | 4067 | 28500 | 14.27%
[29 empty] | 2019 | May | 24 | 7 | 13834.5 | 28500 | 48.54%
[29 empty] | 2019 | May | 24 | 8 | 23388.5 | 28500 | 82.06%
[29 empty] | 2019 | May | 24 | 9 | 31129 | 28500 | 109.2%
[29 empty] | 2019 | May | 24 | 10 | 35908 | 28500 | 126%
[29 empty] | 2019 | May | 24 | 11 | 25952 | 28500 | 91.06%
[29 empty] | 2019 | May | 24 | 12 | 30695 | 28500 | 107.7%
[29 empty] | 2019 | May | 24 | 13 | 22684 | 28500 | 79.59%
[29 empty] | 2019 | May | 24 | 14 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 24 | 15 | 3937.5 | 28500 | 13.82%
[29 empty] | 2019 | May | 24 | 16 | 5183 | 28500 | 18.19%
[29 empty] | 2019 | May | 24 | 17 | 2497 | 28500 | 8.761%
[29 empty] | 2019 | May | 24 | 18 | 399 | 28500 | 1.4%
[29 empty] | 2019 | May | 24 | 19 | 92.5 | 28500 | 0.3246%
[29 empty] | 2019 | May | 24 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 24 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 24 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 24 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 25 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 25 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 25 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 25 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 25 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 25 | 5 | 1444.5 | 28500 | 5.068%
[29 empty] | 2019 | May | 25 | 6 | 4863.5 | 28500 | 17.06%
[29 empty] | 2019 | May | 25 | 7 | 7477.5 | 28500 | 26.24%
[29 empty] | 2019 | May | 25 | 8 | 3788.5 | 28500 | 13.29%
[29 empty] | 2019 | May | 25 | 9 | 24008 | 28500 | 84.24%
[29 empty] | 2019 | May | 25 | 10 | 20479 | 28500 | 71.86%
[29 empty] | 2019 | May | 25 | 11 | 8876.5 | 28500 | 31.15%
[29 empty] | 2019 | May | 25 | 12 | 35209 | 28500 | 123.5%
[29 empty] | 2019 | May | 25 | 13 | 33516.5 | 28500 | 117.6%
[29 empty] | 2019 | May | 25 | 14 | 23063.5 | 28500 | 80.92%
[29 empty] | 2019 | May | 25 | 15 | 21516 | 28500 | 75.49%
[29 empty] | 2019 | May | 25 | 16 | 12199 | 28500 | 42.8%
[29 empty] | 2019 | May | 25 | 17 | 8324 | 28500 | 29.21%
[29 empty] | 2019 | May | 25 | 18 | 2816 | 28500 | 9.881%
[29 empty] | 2019 | May | 25 | 19 | 52.5 | 28500 | 0.1842%
[29 empty] | 2019 | May | 25 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 25 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 25 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 25 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 26 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 26 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 26 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 26 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 26 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 26 | 5 | 925 | 28500 | 3.246%
[29 empty] | 2019 | May | 26 | 6 | 4293.5 | 28500 | 15.06%
[29 empty] | 2019 | May | 26 | 7 | 11059 | 28500 | 38.8%
[29 empty] | 2019 | May | 26 | 8 | 19888.5 | 28500 | 69.78%
[29 empty] | 2019 | May | 26 | 9 | 29514.5 | 28500 | 103.6%
[29 empty] | 2019 | May | 26 | 10 | 31854 | 28500 | 111.8%
[29 empty] | 2019 | May | 26 | 11 | 38135 | 28500 | 133.8%
[29 empty] | 2019 | May | 26 | 12 | 20366 | 28500 | 71.46%
[29 empty] | 2019 | May | 26 | 13 | 13372 | 28500 | 46.92%
[29 empty] | 2019 | May | 26 | 14 | 6593 | 28500 | 23.13%
[29 empty] | 2019 | May | 26 | 15 | 4527 | 28500 | 15.88%
[29 empty] | 2019 | May | 26 | 16 | 4377.5 | 28500 | 15.36%
[29 empty] | 2019 | May | 26 | 17 | 1661.5 | 28500 | 5.83%
[29 empty] | 2019 | May | 26 | 18 | 742.5 | 28500 | 2.605%
[29 empty] | 2019 | May | 26 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 26 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 26 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 26 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 26 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 27 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 27 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 27 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 27 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 27 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 27 | 5 | 1358 | 28500 | 4.765%
[29 empty] | 2019 | May | 27 | 6 | 4486 | 28500 | 15.74%
[29 empty] | 2019 | May | 27 | 7 | 11614 | 28500 | 40.75%
[29 empty] | 2019 | May | 27 | 8 | 3753 | 28500 | 13.17%
[29 empty] | 2019 | May | 27 | 9 | 27339 | 28500 | 95.93%
[29 empty] | 2019 | May | 27 | 10 | 32603 | 28500 | 114.4%
[29 empty] | 2019 | May | 27 | 11 | 20409 | 28500 | 71.61%
[29 empty] | 2019 | May | 27 | 12 | 32133 | 28500 | 112.7%
[29 empty] | 2019 | May | 27 | 13 | 3385 | 28500 | 11.88%
[29 empty] | 2019 | May | 27 | 14 | 7105.5 | 28500 | 24.93%
[29 empty] | 2019 | May | 27 | 15 | 16286 | 28500 | 57.14%
[29 empty] | 2019 | May | 27 | 16 | 9548.5 | 28500 | 33.5%
[29 empty] | 2019 | May | 27 | 17 | 679 | 28500 | 2.382%
[29 empty] | 2019 | May | 27 | 18 | 1317.5 | 28500 | 4.623%
[29 empty] | 2019 | May | 27 | 19 | 115.5 | 28500 | 0.4053%
[29 empty] | 2019 | May | 27 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 27 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 27 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 27 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 28 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 28 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 28 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 28 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 28 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 28 | 5 | 1701.5 | 28500 | 5.97%
[29 empty] | 2019 | May | 28 | 6 | 4990.5 | 28500 | 17.51%
[29 empty] | 2019 | May | 28 | 7 | 9778 | 28500 | 34.31%
[29 empty] | 2019 | May | 28 | 8 | 16217.5 | 28500 | 56.9%
[29 empty] | 2019 | May | 28 | 9 | 15706 | 28500 | 55.11%
[29 empty] | 2019 | May | 28 | 10 | 2820.5 | 28500 | 9.896%
[29 empty] | 2019 | May | 28 | 11 | 3987.5 | 28500 | 13.99%
[29 empty] | 2019 | May | 28 | 12 | 28218.5 | 28500 | 99.01%
[29 empty] | 2019 | May | 28 | 13 | 18560.5 | 28500 | 65.12%
[29 empty] | 2019 | May | 28 | 14 | 6483.5 | 28500 | 22.75%
[29 empty] | 2019 | May | 28 | 15 | 4268.5 | 28500 | 14.98%
[29 empty] | 2019 | May | 28 | 16 | 9074.5 | 28500 | 31.84%
[29 empty] | 2019 | May | 28 | 17 | 5663.5 | 28500 | 19.87%
[29 empty] | 2019 | May | 28 | 18 | 3000 | 28500 | 10.53%
[29 empty] | 2019 | May | 28 | 19 | 706 | 28500 | 2.477%
[29 empty] | 2019 | May | 28 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 28 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 28 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 28 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 29 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 29 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 29 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 29 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 29 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 29 | 5 | 1494.5 | 28500 | 5.244%
[29 empty] | 2019 | May | 29 | 6 | 4322.5 | 28500 | 15.17%
[29 empty] | 2019 | May | 29 | 7 | 7989.5 | 28500 | 28.03%
[29 empty] | 2019 | May | 29 | 8 | 12538 | 28500 | 43.99%
[29 empty] | 2019 | May | 29 | 9 | 22722 | 28500 | 79.73%
[29 empty] | 2019 | May | 29 | 10 | 12946.5 | 28500 | 45.43%
[29 empty] | 2019 | May | 29 | 11 | 21832.5 | 28500 | 76.61%
[29 empty] | 2019 | May | 29 | 12 | 19987 | 28500 | 70.13%
[29 empty] | 2019 | May | 29 | 13 | 8281 | 28500 | 29.06%
[29 empty] | 2019 | May | 29 | 14 | 7457.5 | 28500 | 26.17%
[29 empty] | 2019 | May | 29 | 15 | 3368 | 28500 | 11.82%
[29 empty] | 2019 | May | 29 | 16 | 2578.5 | 28500 | 9.047%
[29 empty] | 2019 | May | 29 | 17 | 920 | 28500 | 3.228%
[29 empty] | 2019 | May | 29 | 18 | 323.5 | 28500 | 1.135%
[29 empty] | 2019 | May | 29 | 19 | 37 | 28500 | 0.1298%
[29 empty] | 2019 | May | 29 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 29 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 29 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 29 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 30 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 30 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 30 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 30 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 30 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 30 | 5 | 1268 | 28500 | 4.449%
[29 empty] | 2019 | May | 30 | 6 | 5017.5 | 28500 | 17.61%
[29 empty] | 2019 | May | 30 | 7 | 13312 | 28500 | 46.71%
[29 empty] | 2019 | May | 30 | 8 | 23186 | 28500 | 81.35%
[29 empty] | 2019 | May | 30 | 9 | 15450.5 | 28500 | 54.21%
[29 empty] | 2019 | May | 30 | 10 | 30848 | 28500 | 108.2%
[29 empty] | 2019 | May | 30 | 11 | 16206.5 | 28500 | 56.86%
[29 empty] | 2019 | May | 30 | 12 | 6939.5 | 28500 | 24.35%
[29 empty] | 2019 | May | 30 | 13 | 18995.5 | 28500 | 66.65%
[29 empty] | 2019 | May | 30 | 14 | 4974 | 28500 | 17.45%
[29 empty] | 2019 | May | 30 | 15 | 8015 | 28500 | 28.12%
[29 empty] | 2019 | May | 30 | 16 | 8968 | 28500 | 31.47%
[29 empty] | 2019 | May | 30 | 17 | 3020.5 | 28500 | 10.6%
[29 empty] | 2019 | May | 30 | 18 | 2360 | 28500 | 8.281%
[29 empty] | 2019 | May | 30 | 19 | 430.5 | 28500 | 1.511%
[29 empty] | 2019 | May | 30 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 30 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 30 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 30 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 31 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 31 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 31 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 31 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 31 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 31 | 5 | 590.5 | 28500 | 2.072%
[29 empty] | 2019 | May | 31 | 6 | 2639.5 | 28500 | 9.261%
[29 empty] | 2019 | May | 31 | 7 | 3143.5 | 28500 | 11.03%
[29 empty] | 2019 | May | 31 | 8 | 9725 | 28500 | 34.12%
[29 empty] | 2019 | May | 31 | 9 | 12622 | 28500 | 44.29%
[29 empty] | 2019 | May | 31 | 10 | 5492 | 28500 | 19.27%
[29 empty] | 2019 | May | 31 | 11 | 11638.5 | 28500 | 40.84%
[29 empty] | 2019 | May | 31 | 12 | 4896 | 28500 | 17.18%
[29 empty] | 2019 | May | 31 | 13 | 4582 | 28500 | 16.08%
[29 empty] | 2019 | May | 31 | 14 | 5899.5 | 28500 | 20.7%
[29 empty] | 2019 | May | 31 | 15 | 12279.5 | 28500 | 43.09%
[29 empty] | 2019 | May | 31 | 16 | 12468.5 | 28500 | 43.75%
[29 empty] | 2019 | May | 31 | 17 | 8870 | 28500 | 31.12%
[29 empty] | 2019 | May | 31 | 18 | 2853 | 28500 | 10.01%
[29 empty] | 2019 | May | 31 | 19 | 750 | 28500 | 2.632%
[29 empty] | 2019 | May | 31 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 31 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 31 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | May | 31 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 1 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 1 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 1 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 1 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 1 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 1 | 5 | 1616 | 28500 | 5.67%
[29 empty] | 2019 | June | 1 | 6 | 4027 | 28500 | 14.13%
[29 empty] | 2019 | June | 1 | 7 | 13696 | 28500 | 48.06%
[29 empty] | 2019 | June | 1 | 8 | 22639.5 | 28500 | 79.44%
[29 empty] | 2019 | June | 1 | 9 | 30342 | 28500 | 106.5%
[29 empty] | 2019 | June | 1 | 10 | 36024 | 28500 | 126.4%
[29 empty] | 2019 | June | 1 | 11 | 38864 | 28500 | 136.4%
[29 empty] | 2019 | June | 1 | 12 | 38181 | 28500 | 134%
[29 empty] | 2019 | June | 1 | 13 | 34782.5 | 28500 | 122%
[29 empty] | 2019 | June | 1 | 14 | 29365.5 | 28500 | 103%
[29 empty] | 2019 | June | 1 | 15 | 23689.5 | 28500 | 83.12%
[29 empty] | 2019 | June | 1 | 16 | 11599 | 28500 | 40.7%
[29 empty] | 2019 | June | 1 | 17 | 8199 | 28500 | 28.77%
[29 empty] | 2019 | June | 1 | 18 | 1228 | 28500 | 4.309%
[29 empty] | 2019 | June | 1 | 19 | 675.5 | 28500 | 2.37%
[29 empty] | 2019 | June | 1 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 1 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 1 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 1 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 2 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 2 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 2 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 2 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 2 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 2 | 5 | 1244.5 | 28500 | 4.367%
[29 empty] | 2019 | June | 2 | 6 | 5045 | 28500 | 17.7%
[29 empty] | 2019 | June | 2 | 7 | 10495.5 | 28500 | 36.83%
[29 empty] | 2019 | June | 2 | 8 | 18310 | 28500 | 64.25%
[29 empty] | 2019 | June | 2 | 9 | 22962.5 | 28500 | 80.57%
[29 empty] | 2019 | June | 2 | 10 | 23146 | 28500 | 81.21%
[29 empty] | 2019 | June | 2 | 11 | 31792.5 | 28500 | 111.6%
[29 empty] | 2019 | June | 2 | 12 | 37319 | 28500 | 130.9%
[29 empty] | 2019 | June | 2 | 13 | 38463.5 | 28500 | 135%
[29 empty] | 2019 | June | 2 | 14 | 21016 | 28500 | 73.74%
[29 empty] | 2019 | June | 2 | 15 | 20103.5 | 28500 | 70.54%
[29 empty] | 2019 | June | 2 | 16 | 18756.5 | 28500 | 65.81%
[29 empty] | 2019 | June | 2 | 17 | 4152 | 28500 | 14.57%
[29 empty] | 2019 | June | 2 | 18 | 2703 | 28500 | 9.484%
[29 empty] | 2019 | June | 2 | 19 | 18.5 | 28500 | 0.06491%
[29 empty] | 2019 | June | 2 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 2 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 2 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 2 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 3 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 3 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 3 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 3 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 3 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 3 | 5 | 1574.5 | 28500 | 5.525%
[29 empty] | 2019 | June | 3 | 6 | 4723 | 28500 | 16.57%
[29 empty] | 2019 | June | 3 | 7 | 13403.5 | 28500 | 47.03%
[29 empty] | 2019 | June | 3 | 8 | 21825.5 | 28500 | 76.58%
[29 empty] | 2019 | June | 3 | 9 | 26302.5 | 28500 | 92.29%
[29 empty] | 2019 | June | 3 | 10 | 21773.5 | 28500 | 76.4%
[29 empty] | 2019 | June | 3 | 11 | 13925 | 28500 | 48.86%
[29 empty] | 2019 | June | 3 | 12 | 10458.5 | 28500 | 36.7%
[29 empty] | 2019 | June | 3 | 13 | 34956 | 28500 | 122.7%
[29 empty] | 2019 | June | 3 | 14 | 9540 | 28500 | 33.47%
[29 empty] | 2019 | June | 3 | 15 | 23366 | 28500 | 81.99%
[29 empty] | 2019 | June | 3 | 16 | 18303 | 28500 | 64.22%
[29 empty] | 2019 | June | 3 | 17 | 9244 | 28500 | 32.44%
[29 empty] | 2019 | June | 3 | 18 | 2349.5 | 28500 | 8.244%
[29 empty] | 2019 | June | 3 | 19 | 876 | 28500 | 3.074%
[29 empty] | 2019 | June | 3 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 3 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 3 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 3 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 4 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 4 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 4 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 4 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 4 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 4 | 5 | 1418.5 | 28500 | 4.977%
[29 empty] | 2019 | June | 4 | 6 | 4080.5 | 28500 | 14.32%
[29 empty] | 2019 | June | 4 | 7 | 7248 | 28500 | 25.43%
[29 empty] | 2019 | June | 4 | 8 | 3989.5 | 28500 | 14%
[29 empty] | 2019 | June | 4 | 9 | 6187 | 28500 | 21.71%
[29 empty] | 2019 | June | 4 | 10 | 6952.5 | 28500 | 24.39%
[29 empty] | 2019 | June | 4 | 11 | 4104.5 | 28500 | 14.4%
[29 empty] | 2019 | June | 4 | 12 | 4904.5 | 28500 | 17.21%
[29 empty] | 2019 | June | 4 | 13 | 2675 | 28500 | 9.386%
[29 empty] | 2019 | June | 4 | 14 | 5152.5 | 28500 | 18.08%
[29 empty] | 2019 | June | 4 | 15 | 2015 | 28500 | 7.07%
[29 empty] | 2019 | June | 4 | 16 | 5418.5 | 28500 | 19.01%
[29 empty] | 2019 | June | 4 | 17 | 4849 | 28500 | 17.01%
[29 empty] | 2019 | June | 4 | 18 | 2643.5 | 28500 | 9.275%
[29 empty] | 2019 | June | 4 | 19 | 876.5 | 28500 | 3.075%
[29 empty] | 2019 | June | 4 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 4 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 4 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 4 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 5 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 5 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 5 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 5 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 5 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 5 | 5 | 1575.5 | 28500 | 5.528%
[29 empty] | 2019 | June | 5 | 6 | 5087 | 28500 | 17.85%
[29 empty] | 2019 | June | 5 | 7 | 13635.5 | 28500 | 47.84%
[29 empty] | 2019 | June | 5 | 8 | 19616.5 | 28500 | 68.83%
[29 empty] | 2019 | June | 5 | 9 | 24457 | 28500 | 85.81%
[29 empty] | 2019 | June | 5 | 10 | 23551.5 | 28500 | 82.64%
[29 empty] | 2019 | June | 5 | 11 | 22419 | 28500 | 78.66%
[29 empty] | 2019 | June | 5 | 12 | 19231 | 28500 | 67.48%
[29 empty] | 2019 | June | 5 | 13 | 5805 | 28500 | 20.37%
[29 empty] | 2019 | June | 5 | 14 | 10091.5 | 28500 | 35.41%
[29 empty] | 2019 | June | 5 | 15 | 7061.5 | 28500 | 24.78%
[29 empty] | 2019 | June | 5 | 16 | 3340.5 | 28500 | 11.72%
[29 empty] | 2019 | June | 5 | 17 | 5575.5 | 28500 | 19.56%
[29 empty] | 2019 | June | 5 | 18 | 2771 | 28500 | 9.723%
[29 empty] | 2019 | June | 5 | 19 | 37 | 28500 | 0.1298%
[29 empty] | 2019 | June | 5 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 5 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 5 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 5 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 6 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 6 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 6 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 6 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 6 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 6 | 5 | 2001.5 | 28500 | 7.023%
[29 empty] | 2019 | June | 6 | 6 | 4136 | 28500 | 14.51%
[29 empty] | 2019 | June | 6 | 7 | 14247.5 | 28500 | 49.99%
[29 empty] | 2019 | June | 6 | 8 | 23847 | 28500 | 83.67%
[29 empty] | 2019 | June | 6 | 9 | 23102 | 28500 | 81.06%
[29 empty] | 2019 | June | 6 | 10 | 16545 | 28500 | 58.05%
[29 empty] | 2019 | June | 6 | 11 | 14868 | 28500 | 52.17%
[29 empty] | 2019 | June | 6 | 12 | 42274 | 28500 | 148.3%
[29 empty] | 2019 | June | 6 | 13 | 39733 | 28500 | 139.4%
[29 empty] | 2019 | June | 6 | 14 | 34604 | 28500 | 121.4%
[29 empty] | 2019 | June | 6 | 15 | 29744 | 28500 | 104.4%
[29 empty] | 2019 | June | 6 | 16 | 20036 | 28500 | 70.3%
[29 empty] | 2019 | June | 6 | 17 | 9510 | 28500 | 33.37%
[29 empty] | 2019 | June | 6 | 18 | 2058.5 | 28500 | 7.223%
[29 empty] | 2019 | June | 6 | 19 | 941.5 | 28500 | 3.304%
[29 empty] | 2019 | June | 6 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 6 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 6 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 6 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 7 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 7 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 7 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 7 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 7 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 7 | 5 | 140 | 28500 | 0.4912%
[29 empty] | 2019 | June | 7 | 6 | 597.5 | 28500 | 2.096%
[29 empty] | 2019 | June | 7 | 7 | 1612 | 28500 | 5.656%
[29 empty] | 2019 | June | 7 | 8 | 5027 | 28500 | 17.64%
[29 empty] | 2019 | June | 7 | 9 | 5699 | 28500 | 20%
[29 empty] | 2019 | June | 7 | 10 | 4638 | 28500 | 16.27%
[29 empty] | 2019 | June | 7 | 11 | 2677.5 | 28500 | 9.395%
[29 empty] | 2019 | June | 7 | 12 | 7239 | 28500 | 25.4%
[29 empty] | 2019 | June | 7 | 13 | 8926.5 | 28500 | 31.32%
[29 empty] | 2019 | June | 7 | 14 | 13509 | 28500 | 47.4%
[29 empty] | 2019 | June | 7 | 15 | 18443.5 | 28500 | 64.71%
[29 empty] | 2019 | June | 7 | 16 | 4000 | 28500 | 14.04%
[29 empty] | 2019 | June | 7 | 17 | 6204 | 28500 | 21.77%
[29 empty] | 2019 | June | 7 | 18 | 1046 | 28500 | 3.67%
[29 empty] | 2019 | June | 7 | 19 | 823.5 | 28500 | 2.889%
[29 empty] | 2019 | June | 7 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 7 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 7 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 7 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 8 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 8 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 8 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 8 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 8 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 8 | 5 | 537 | 28500 | 1.884%
[29 empty] | 2019 | June | 8 | 6 | 477 | 28500 | 1.674%
[29 empty] | 2019 | June | 8 | 7 | 7862 | 28500 | 27.59%
[29 empty] | 2019 | June | 8 | 8 | 10130.5 | 28500 | 35.55%
[29 empty] | 2019 | June | 8 | 9 | 8823.5 | 28500 | 30.96%
[29 empty] | 2019 | June | 8 | 10 | 14487 | 28500 | 50.83%
[29 empty] | 2019 | June | 8 | 11 | 23598.5 | 28500 | 82.8%
[29 empty] | 2019 | June | 8 | 12 | 36354.5 | 28500 | 127.6%
[29 empty] | 2019 | June | 8 | 13 | 30591 | 28500 | 107.3%
[29 empty] | 2019 | June | 8 | 14 | 20178.5 | 28500 | 70.8%
[29 empty] | 2019 | June | 8 | 15 | 28046 | 28500 | 98.41%
[29 empty] | 2019 | June | 8 | 16 | 15625.5 | 28500 | 54.83%
[29 empty] | 2019 | June | 8 | 17 | 5842 | 28500 | 20.5%
[29 empty] | 2019 | June | 8 | 18 | 1477 | 28500 | 5.182%
[29 empty] | 2019 | June | 8 | 19 | 761.5 | 28500 | 2.672%
[29 empty] | 2019 | June | 8 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 8 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 8 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 8 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 9 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 9 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 9 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 9 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 9 | 4 | 58 | 28500 | 0.2035%
[29 empty] | 2019 | June | 9 | 5 | 2002.5 | 28500 | 7.026%
[29 empty] | 2019 | June | 9 | 6 | 4628 | 28500 | 16.24%
[29 empty] | 2019 | June | 9 | 7 | 13586 | 28500 | 47.67%
[29 empty] | 2019 | June | 9 | 8 | 20467 | 28500 | 71.81%
[29 empty] | 2019 | June | 9 | 9 | 27202 | 28500 | 95.45%
[29 empty] | 2019 | June | 9 | 10 | 31323 | 28500 | 109.9%
[29 empty] | 2019 | June | 9 | 11 | 30132 | 28500 | 105.7%
[29 empty] | 2019 | June | 9 | 12 | 26485.5 | 28500 | 92.93%
[29 empty] | 2019 | June | 9 | 13 | 11286.5 | 28500 | 39.6%
[29 empty] | 2019 | June | 9 | 14 | 9363 | 28500 | 32.85%
[29 empty] | 2019 | June | 9 | 15 | 13013 | 28500 | 45.66%
[29 empty] | 2019 | June | 9 | 16 | 13704 | 28500 | 48.08%
[29 empty] | 2019 | June | 9 | 17 | 4019 | 28500 | 14.1%
[29 empty] | 2019 | June | 9 | 18 | 2345 | 28500 | 8.228%
[29 empty] | 2019 | June | 9 | 19 | 1061 | 28500 | 3.723%
[29 empty] | 2019 | June | 9 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 9 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 9 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 9 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 10 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 10 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 10 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 10 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 10 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 10 | 5 | 929 | 28500 | 3.26%
[29 empty] | 2019 | June | 10 | 6 | 475 | 28500 | 1.667%
[29 empty] | 2019 | June | 10 | 7 | 1947 | 28500 | 6.832%
[29 empty] | 2019 | June | 10 | 8 | 3033.5 | 28500 | 10.64%
[29 empty] | 2019 | June | 10 | 9 | 3497 | 28500 | 12.27%
[29 empty] | 2019 | June | 10 | 10 | 2965 | 28500 | 10.4%
[29 empty] | 2019 | June | 10 | 11 | 2662 | 28500 | 9.34%
[29 empty] | 2019 | June | 10 | 12 | 2700.5 | 28500 | 9.475%
[29 empty] | 2019 | June | 10 | 13 | 2284.5 | 28500 | 8.016%
[29 empty] | 2019 | June | 10 | 14 | 4625 | 28500 | 16.23%
[29 empty] | 2019 | June | 10 | 15 | 2697.5 | 28500 | 9.465%
[29 empty] | 2019 | June | 10 | 16 | 1878.5 | 28500 | 6.591%
[29 empty] | 2019 | June | 10 | 17 | 759.5 | 28500 | 2.665%
[29 empty] | 2019 | June | 10 | 18 | 3357 | 28500 | 11.78%
[29 empty] | 2019 | June | 10 | 19 | 314 | 28500 | 1.102%
[29 empty] | 2019 | June | 10 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 10 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 10 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 10 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 11 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 11 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 11 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 11 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 11 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 11 | 5 | 2019 | 28500 | 7.084%
[29 empty] | 2019 | June | 11 | 6 | 3962.5 | 28500 | 13.9%
[29 empty] | 2019 | June | 11 | 7 | 14077.5 | 28500 | 49.39%
[29 empty] | 2019 | June | 11 | 8 | 19996.5 | 28500 | 70.16%
[29 empty] | 2019 | June | 11 | 9 | 17518.5 | 28500 | 61.47%
[29 empty] | 2019 | June | 11 | 10 | 32455 | 28500 | 113.9%
[29 empty] | 2019 | June | 11 | 11 | 29506.5 | 28500 | 103.5%
[29 empty] | 2019 | June | 11 | 12 | 27828 | 28500 | 97.64%
[29 empty] | 2019 | June | 11 | 13 | 28260 | 28500 | 99.16%
[29 empty] | 2019 | June | 11 | 14 | 21386 | 28500 | 75.04%
[29 empty] | 2019 | June | 11 | 15 | 14118.5 | 28500 | 49.54%
[29 empty] | 2019 | June | 11 | 16 | 14565.5 | 28500 | 51.11%
[29 empty] | 2019 | June | 11 | 17 | 3250.5 | 28500 | 11.41%
[29 empty] | 2019 | June | 11 | 18 | 3413 | 28500 | 11.98%
[29 empty] | 2019 | June | 11 | 19 | 1101.5 | 28500 | 3.865%
[29 empty] | 2019 | June | 11 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 11 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 11 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 11 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 12 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 12 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 12 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 12 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 12 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 12 | 5 | 1885.5 | 28500 | 6.616%
[29 empty] | 2019 | June | 12 | 6 | 2892 | 28500 | 10.15%
[29 empty] | 2019 | June | 12 | 7 | 11194 | 28500 | 39.28%
[29 empty] | 2019 | June | 12 | 8 | 19828 | 28500 | 69.57%
[29 empty] | 2019 | June | 12 | 9 | 22326.5 | 28500 | 78.34%
[29 empty] | 2019 | June | 12 | 10 | 8823 | 28500 | 30.96%
[29 empty] | 2019 | June | 12 | 11 | 4928.5 | 28500 | 17.29%
[29 empty] | 2019 | June | 12 | 12 | 7298 | 28500 | 25.61%
[29 empty] | 2019 | June | 12 | 13 | 4819 | 28500 | 16.91%
[29 empty] | 2019 | June | 12 | 14 | 4006.5 | 28500 | 14.06%
[29 empty] | 2019 | June | 12 | 15 | 3163 | 28500 | 11.1%
[29 empty] | 2019 | June | 12 | 16 | 4577.5 | 28500 | 16.06%
[29 empty] | 2019 | June | 12 | 17 | 5641.5 | 28500 | 19.79%
[29 empty] | 2019 | June | 12 | 18 | 2185.5 | 28500 | 7.668%
[29 empty] | 2019 | June | 12 | 19 | 981 | 28500 | 3.442%
[29 empty] | 2019 | June | 12 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 12 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 12 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 12 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 13 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 13 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 13 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 13 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 13 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 13 | 5 | 479.5 | 28500 | 1.682%
[29 empty] | 2019 | June | 13 | 6 | 4123.5 | 28500 | 14.47%
[29 empty] | 2019 | June | 13 | 7 | 5728.5 | 28500 | 20.1%
[29 empty] | 2019 | June | 13 | 8 | 12723 | 28500 | 44.64%
[29 empty] | 2019 | June | 13 | 9 | 20917.5 | 28500 | 73.39%
[29 empty] | 2019 | June | 13 | 10 | 16943.5 | 28500 | 59.45%
[29 empty] | 2019 | June | 13 | 11 | 19236 | 28500 | 67.49%
[29 empty] | 2019 | June | 13 | 12 | 10634 | 28500 | 37.31%
[29 empty] | 2019 | June | 13 | 13 | 4319 | 28500 | 15.15%
[29 empty] | 2019 | June | 13 | 14 | 7392.5 | 28500 | 25.94%
[29 empty] | 2019 | June | 13 | 15 | 10306 | 28500 | 36.16%
[29 empty] | 2019 | June | 13 | 16 | 6138.5 | 28500 | 21.54%
[29 empty] | 2019 | June | 13 | 17 | 6442.5 | 28500 | 22.61%
[29 empty] | 2019 | June | 13 | 18 | 920 | 28500 | 3.228%
[29 empty] | 2019 | June | 13 | 19 | 4 | 28500 | 0.01404%
[29 empty] | 2019 | June | 13 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 13 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 13 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 13 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 14 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 14 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 14 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 14 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 14 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 14 | 5 | 1606.5 | 28500 | 5.637%
[29 empty] | 2019 | June | 14 | 6 | 5252 | 28500 | 18.43%
[29 empty] | 2019 | June | 14 | 7 | 8567.5 | 28500 | 30.06%
[29 empty] | 2019 | June | 14 | 8 | 15144.5 | 28500 | 53.14%
[29 empty] | 2019 | June | 14 | 9 | 16938 | 28500 | 59.43%
[29 empty] | 2019 | June | 14 | 10 | 22041.5 | 28500 | 77.34%
[29 empty] | 2019 | June | 14 | 11 | 30531 | 28500 | 107.1%
[29 empty] | 2019 | June | 14 | 12 | 21215.5 | 28500 | 74.44%
[29 empty] | 2019 | June | 14 | 13 | 23389 | 28500 | 82.07%
[29 empty] | 2019 | June | 14 | 14 | 15439.5 | 28500 | 54.17%
[29 empty] | 2019 | June | 14 | 15 | 14555.5 | 28500 | 51.07%
[29 empty] | 2019 | June | 14 | 16 | 18795 | 28500 | 65.95%
[29 empty] | 2019 | June | 14 | 17 | 9674.5 | 28500 | 33.95%
[29 empty] | 2019 | June | 14 | 18 | 2835 | 28500 | 9.947%
[29 empty] | 2019 | June | 14 | 19 | 907 | 28500 | 3.182%
[29 empty] | 2019 | June | 14 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 14 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 14 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 14 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 15 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 15 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 15 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 15 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 15 | 4 | 141 | 28500 | 0.4947%
[29 empty] | 2019 | June | 15 | 5 | 1312 | 28500 | 4.604%
[29 empty] | 2019 | June | 15 | 6 | 3921 | 28500 | 13.76%
[29 empty] | 2019 | June | 15 | 7 | 13687 | 28500 | 48.02%
[29 empty] | 2019 | June | 15 | 8 | 12685.5 | 28500 | 44.51%
[29 empty] | 2019 | June | 15 | 9 | 28702.5 | 28500 | 100.7%
[29 empty] | 2019 | June | 15 | 10 | 12543.5 | 28500 | 44.01%
[29 empty] | 2019 | June | 15 | 11 | 29695 | 28500 | 104.2%
[29 empty] | 2019 | June | 15 | 12 | 15984.5 | 28500 | 56.09%
[29 empty] | 2019 | June | 15 | 13 | 14610 | 28500 | 51.26%
[29 empty] | 2019 | June | 15 | 14 | 8130.5 | 28500 | 28.53%
[29 empty] | 2019 | June | 15 | 15 | 16761 | 28500 | 58.81%
[29 empty] | 2019 | June | 15 | 16 | 9083 | 28500 | 31.87%
[29 empty] | 2019 | June | 15 | 17 | 8236 | 28500 | 28.9%
[29 empty] | 2019 | June | 15 | 18 | 1146 | 28500 | 4.021%
[29 empty] | 2019 | June | 15 | 19 | 1134 | 28500 | 3.979%
[29 empty] | 2019 | June | 15 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 15 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 15 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 15 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 16 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 16 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 16 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 16 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 16 | 4 | 38.5 | 28500 | 0.1351%
[29 empty] | 2019 | June | 16 | 5 | 1448 | 28500 | 5.081%
[29 empty] | 2019 | June | 16 | 6 | 5144.5 | 28500 | 18.05%
[29 empty] | 2019 | June | 16 | 7 | 11914 | 28500 | 41.8%
[29 empty] | 2019 | June | 16 | 8 | 11838 | 28500 | 41.54%
[29 empty] | 2019 | June | 16 | 9 | 6203.5 | 28500 | 21.77%
[29 empty] | 2019 | June | 16 | 10 | 11374 | 28500 | 39.91%
[29 empty] | 2019 | June | 16 | 11 | 18272 | 28500 | 64.11%
[29 empty] | 2019 | June | 16 | 12 | 31648 | 28500 | 111%
[29 empty] | 2019 | June | 16 | 13 | 21130 | 28500 | 74.14%
[29 empty] | 2019 | June | 16 | 14 | 12809.5 | 28500 | 44.95%
[29 empty] | 2019 | June | 16 | 15 | 10272.5 | 28500 | 36.04%
[29 empty] | 2019 | June | 16 | 16 | 13221.5 | 28500 | 46.39%
[29 empty] | 2019 | June | 16 | 17 | 9698 | 28500 | 34.03%
[29 empty] | 2019 | June | 16 | 18 | 3502 | 28500 | 12.29%
[29 empty] | 2019 | June | 16 | 19 | 905 | 28500 | 3.175%
[29 empty] | 2019 | June | 16 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 16 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 16 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 16 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 17 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 17 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 17 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 17 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 17 | 4 | 76 | 28500 | 0.2667%
[29 empty] | 2019 | June | 17 | 5 | 1702 | 28500 | 5.972%
[29 empty] | 2019 | June | 17 | 6 | 4538.5 | 28500 | 15.92%
[29 empty] | 2019 | June | 17 | 7 | 9884.5 | 28500 | 34.68%
[29 empty] | 2019 | June | 17 | 8 | 17723.5 | 28500 | 62.19%
[29 empty] | 2019 | June | 17 | 9 | 26363 | 28500 | 92.5%
[29 empty] | 2019 | June | 17 | 10 | 35576 | 28500 | 124.8%
[29 empty] | 2019 | June | 17 | 11 | 38636 | 28500 | 135.6%
[29 empty] | 2019 | June | 17 | 12 | 41613.5 | 28500 | 146%
[29 empty] | 2019 | June | 17 | 13 | 38569.5 | 28500 | 135.3%
[29 empty] | 2019 | June | 17 | 14 | 35180.5 | 28500 | 123.4%
[29 empty] | 2019 | June | 17 | 15 | 28484.5 | 28500 | 99.95%
[29 empty] | 2019 | June | 17 | 16 | 19462.5 | 28500 | 68.29%
[29 empty] | 2019 | June | 17 | 17 | 5969 | 28500 | 20.94%
[29 empty] | 2019 | June | 17 | 18 | 707.5 | 28500 | 2.482%
[29 empty] | 2019 | June | 17 | 19 | 606.5 | 28500 | 2.128%
[29 empty] | 2019 | June | 17 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 17 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 17 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 17 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 18 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 18 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 18 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 18 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 18 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 18 | 5 | 1953 | 28500 | 6.853%
[29 empty] | 2019 | June | 18 | 6 | 5107 | 28500 | 17.92%
[29 empty] | 2019 | June | 18 | 7 | 8246.5 | 28500 | 28.94%
[29 empty] | 2019 | June | 18 | 8 | 17513 | 28500 | 61.45%
[29 empty] | 2019 | June | 18 | 9 | 28743 | 28500 | 100.9%
[29 empty] | 2019 | June | 18 | 10 | 7757 | 28500 | 27.22%
[29 empty] | 2019 | June | 18 | 11 | 6215.5 | 28500 | 21.81%
[29 empty] | 2019 | June | 18 | 12 | 4060 | 28500 | 14.25%
[29 empty] | 2019 | June | 18 | 13 | 14343.5 | 28500 | 50.33%
[29 empty] | 2019 | June | 18 | 14 | 11587 | 28500 | 40.66%
[29 empty] | 2019 | June | 18 | 15 | 4191 | 28500 | 14.71%
[29 empty] | 2019 | June | 18 | 16 | 2273 | 28500 | 7.975%
[29 empty] | 2019 | June | 18 | 17 | 3718.5 | 28500 | 13.05%
[29 empty] | 2019 | June | 18 | 18 | 1540.5 | 28500 | 5.405%
[29 empty] | 2019 | June | 18 | 19 | 871 | 28500 | 3.056%
[29 empty] | 2019 | June | 18 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 18 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 18 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 18 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 19 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 19 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 19 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 19 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 19 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 19 | 5 | 954.5 | 28500 | 3.349%
[29 empty] | 2019 | June | 19 | 6 | 1222.5 | 28500 | 4.289%
[29 empty] | 2019 | June | 19 | 7 | 2247.5 | 28500 | 7.886%
[29 empty] | 2019 | June | 19 | 8 | 4283.5 | 28500 | 15.03%
[29 empty] | 2019 | June | 19 | 9 | 12659.5 | 28500 | 44.42%
[29 empty] | 2019 | June | 19 | 10 | 7038.5 | 28500 | 24.7%
[29 empty] | 2019 | June | 19 | 11 | 15618.5 | 28500 | 54.8%
[29 empty] | 2019 | June | 19 | 12 | 9759 | 28500 | 34.24%
[29 empty] | 2019 | June | 19 | 13 | 7797 | 28500 | 27.36%
[29 empty] | 2019 | June | 19 | 14 | 9333.5 | 28500 | 32.75%
[29 empty] | 2019 | June | 19 | 15 | 11596.5 | 28500 | 40.69%
[29 empty] | 2019 | June | 19 | 16 | 11790 | 28500 | 41.37%
[29 empty] | 2019 | June | 19 | 17 | 4334.5 | 28500 | 15.21%
[29 empty] | 2019 | June | 19 | 18 | 1092.5 | 28500 | 3.833%
[29 empty] | 2019 | June | 19 | 19 | 1054 | 28500 | 3.698%
[29 empty] | 2019 | June | 19 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 19 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 19 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 19 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 20 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 20 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 20 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 20 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 20 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 20 | 5 | 1467 | 28500 | 5.147%
[29 empty] | 2019 | June | 20 | 6 | 3961 | 28500 | 13.9%
[29 empty] | 2019 | June | 20 | 7 | 13634 | 28500 | 47.84%
[29 empty] | 2019 | June | 20 | 8 | 22936.5 | 28500 | 80.48%
[29 empty] | 2019 | June | 20 | 9 | 30158.5 | 28500 | 105.8%
[29 empty] | 2019 | June | 20 | 10 | 27547.5 | 28500 | 96.66%
[29 empty] | 2019 | June | 20 | 11 | 4253.5 | 28500 | 14.92%
[29 empty] | 2019 | June | 20 | 12 | 20003.5 | 28500 | 70.19%
[29 empty] | 2019 | June | 20 | 13 | 3528 | 28500 | 12.38%
[29 empty] | 2019 | June | 20 | 14 | 4897 | 28500 | 17.18%
[29 empty] | 2019 | June | 20 | 15 | 7755.5 | 28500 | 27.21%
[29 empty] | 2019 | June | 20 | 16 | 17631.5 | 28500 | 61.86%
[29 empty] | 2019 | June | 20 | 17 | 9346 | 28500 | 32.79%
[29 empty] | 2019 | June | 20 | 18 | 3417 | 28500 | 11.99%
[29 empty] | 2019 | June | 20 | 19 | 1188 | 28500 | 4.168%
[29 empty] | 2019 | June | 20 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 20 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 20 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 20 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 21 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 21 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 21 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 21 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 21 | 4 | 77.5 | 28500 | 0.2719%
[29 empty] | 2019 | June | 21 | 5 | 1623.5 | 28500 | 5.696%
[29 empty] | 2019 | June | 21 | 6 | 3916 | 28500 | 13.74%
[29 empty] | 2019 | June | 21 | 7 | 13783 | 28500 | 48.36%
[29 empty] | 2019 | June | 21 | 8 | 22904.5 | 28500 | 80.37%
[29 empty] | 2019 | June | 21 | 9 | 30163 | 28500 | 105.8%
[29 empty] | 2019 | June | 21 | 10 | 28845 | 28500 | 101.2%
[29 empty] | 2019 | June | 21 | 11 | 24168 | 28500 | 84.8%
[29 empty] | 2019 | June | 21 | 12 | 34236 | 28500 | 120.1%
[29 empty] | 2019 | June | 21 | 13 | 32253 | 28500 | 113.2%
[29 empty] | 2019 | June | 21 | 14 | 24591.5 | 28500 | 86.29%
[29 empty] | 2019 | June | 21 | 15 | 19836.5 | 28500 | 69.6%
[29 empty] | 2019 | June | 21 | 16 | 12869 | 28500 | 45.15%
[29 empty] | 2019 | June | 21 | 17 | 4391 | 28500 | 15.41%
[29 empty] | 2019 | June | 21 | 18 | 1300 | 28500 | 4.561%
[29 empty] | 2019 | June | 21 | 19 | 689.5 | 28500 | 2.419%
[29 empty] | 2019 | June | 21 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 21 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 21 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 21 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 22 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 22 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 22 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 22 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 22 | 4 | 98.5 | 28500 | 0.3456%
[29 empty] | 2019 | June | 22 | 5 | 1514.5 | 28500 | 5.314%
[29 empty] | 2019 | June | 22 | 6 | 3851 | 28500 | 13.51%
[29 empty] | 2019 | June | 22 | 7 | 13044 | 28500 | 45.77%
[29 empty] | 2019 | June | 22 | 8 | 22712.5 | 28500 | 79.69%
[29 empty] | 2019 | June | 22 | 9 | 31835 | 28500 | 111.7%
[29 empty] | 2019 | June | 22 | 10 | 36003 | 28500 | 126.3%
[29 empty] | 2019 | June | 22 | 11 | 34356 | 28500 | 120.5%
[29 empty] | 2019 | June | 22 | 12 | 25544.5 | 28500 | 89.63%
[29 empty] | 2019 | June | 22 | 13 | 22613 | 28500 | 79.34%
[29 empty] | 2019 | June | 22 | 14 | 25368 | 28500 | 89.01%
[29 empty] | 2019 | June | 22 | 15 | 25990.5 | 28500 | 91.19%
[29 empty] | 2019 | June | 22 | 16 | 20177 | 28500 | 70.8%
[29 empty] | 2019 | June | 22 | 17 | 9989.5 | 28500 | 35.05%
[29 empty] | 2019 | June | 22 | 18 | 3321 | 28500 | 11.65%
[29 empty] | 2019 | June | 22 | 19 | 901.5 | 28500 | 3.163%
[29 empty] | 2019 | June | 22 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 22 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 22 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 22 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 23 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 23 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 23 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 23 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 23 | 4 | 37.5 | 28500 | 0.1316%
[29 empty] | 2019 | June | 23 | 5 | 645 | 28500 | 2.263%
[29 empty] | 2019 | June | 23 | 6 | 3706 | 28500 | 13%
[29 empty] | 2019 | June | 23 | 7 | 8410.5 | 28500 | 29.51%
[29 empty] | 2019 | June | 23 | 8 | 15993 | 28500 | 56.12%
[29 empty] | 2019 | June | 23 | 9 | 13358 | 28500 | 46.87%
[29 empty] | 2019 | June | 23 | 10 | 24573.5 | 28500 | 86.22%
[29 empty] | 2019 | June | 23 | 11 | 18003 | 28500 | 63.17%
[29 empty] | 2019 | June | 23 | 12 | 22214.5 | 28500 | 77.95%
[29 empty] | 2019 | June | 23 | 13 | 13960.5 | 28500 | 48.98%
[29 empty] | 2019 | June | 23 | 14 | 19316 | 28500 | 67.78%
[29 empty] | 2019 | June | 23 | 15 | 4685 | 28500 | 16.44%
[29 empty] | 2019 | June | 23 | 16 | 2799 | 28500 | 9.821%
[29 empty] | 2019 | June | 23 | 17 | 1798 | 28500 | 6.309%
[29 empty] | 2019 | June | 23 | 18 | 1419.5 | 28500 | 4.981%
[29 empty] | 2019 | June | 23 | 19 | 71 | 28500 | 0.2491%
[29 empty] | 2019 | June | 23 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 23 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 23 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 23 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 24 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 24 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 24 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 24 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 24 | 4 | 53 | 28500 | 0.186%
[29 empty] | 2019 | June | 24 | 5 | 1425.5 | 28500 | 5.002%
[29 empty] | 2019 | June | 24 | 6 | 1491.5 | 28500 | 5.233%
[29 empty] | 2019 | June | 24 | 7 | 11648 | 28500 | 40.87%
[29 empty] | 2019 | June | 24 | 8 | 10189.5 | 28500 | 35.75%
[29 empty] | 2019 | June | 24 | 9 | 2941.5 | 28500 | 10.32%
[29 empty] | 2019 | June | 24 | 10 | 3529.5 | 28500 | 12.38%
[29 empty] | 2019 | June | 24 | 11 | 9704 | 28500 | 34.05%
[29 empty] | 2019 | June | 24 | 12 | 9386.5 | 28500 | 32.94%
[29 empty] | 2019 | June | 24 | 13 | 6779.5 | 28500 | 23.79%
[29 empty] | 2019 | June | 24 | 14 | 12096 | 28500 | 42.44%
[29 empty] | 2019 | June | 24 | 15 | 15860 | 28500 | 55.65%
[29 empty] | 2019 | June | 24 | 16 | 2587.5 | 28500 | 9.079%
[29 empty] | 2019 | June | 24 | 17 | 1743.5 | 28500 | 6.118%
[29 empty] | 2019 | June | 24 | 18 | 1577.5 | 28500 | 5.535%
[29 empty] | 2019 | June | 24 | 19 | 131.5 | 28500 | 0.4614%
[29 empty] | 2019 | June | 24 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 24 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 24 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 24 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 25 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 25 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 25 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 25 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 25 | 4 | 3 | 28500 | 0.01053%
[29 empty] | 2019 | June | 25 | 5 | 867 | 28500 | 3.042%
[29 empty] | 2019 | June | 25 | 6 | 3064.5 | 28500 | 10.75%
[29 empty] | 2019 | June | 25 | 7 | 4458 | 28500 | 15.64%
[29 empty] | 2019 | June | 25 | 8 | 9971 | 28500 | 34.99%
[29 empty] | 2019 | June | 25 | 9 | 15981.5 | 28500 | 56.08%
[29 empty] | 2019 | June | 25 | 10 | 19136 | 28500 | 67.14%
[29 empty] | 2019 | June | 25 | 11 | 18986.5 | 28500 | 66.62%
[29 empty] | 2019 | June | 25 | 12 | 18433 | 28500 | 64.68%
[29 empty] | 2019 | June | 25 | 13 | 13637 | 28500 | 47.85%
[29 empty] | 2019 | June | 25 | 14 | 10253.5 | 28500 | 35.98%
[29 empty] | 2019 | June | 25 | 15 | 12541.5 | 28500 | 44.01%
[29 empty] | 2019 | June | 25 | 16 | 3763.5 | 28500 | 13.21%
[29 empty] | 2019 | June | 25 | 17 | 7415.5 | 28500 | 26.02%
[29 empty] | 2019 | June | 25 | 18 | 3450.5 | 28500 | 12.11%
[29 empty] | 2019 | June | 25 | 19 | 222.5 | 28500 | 0.7807%
[29 empty] | 2019 | June | 25 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 25 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 25 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 25 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 26 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 26 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 26 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 26 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 26 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 26 | 5 | 74.5 | 28500 | 0.2614%
[29 empty] | 2019 | June | 26 | 6 | 651 | 28500 | 2.284%
[29 empty] | 2019 | June | 26 | 7 | 1210.5 | 28500 | 4.247%
[29 empty] | 2019 | June | 26 | 8 | 3774.5 | 28500 | 13.24%
[29 empty] | 2019 | June | 26 | 9 | 4562 | 28500 | 16.01%
[29 empty] | 2019 | June | 26 | 10 | 5694.5 | 28500 | 19.98%
[29 empty] | 2019 | June | 26 | 11 | 9699 | 28500 | 34.03%
[29 empty] | 2019 | June | 26 | 12 | 17348.5 | 28500 | 60.87%
[29 empty] | 2019 | June | 26 | 13 | 30652 | 28500 | 107.6%
[29 empty] | 2019 | June | 26 | 14 | 30290.5 | 28500 | 106.3%
[29 empty] | 2019 | June | 26 | 15 | 20510 | 28500 | 71.96%
[29 empty] | 2019 | June | 26 | 16 | 11038 | 28500 | 38.73%
[29 empty] | 2019 | June | 26 | 17 | 5736 | 28500 | 20.13%
[29 empty] | 2019 | June | 26 | 18 | 2109.5 | 28500 | 7.402%
[29 empty] | 2019 | June | 26 | 19 | 278 | 28500 | 0.9754%
[29 empty] | 2019 | June | 26 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 26 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 26 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 26 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 27 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 27 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 27 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 27 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 27 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 27 | 5 | 735 | 28500 | 2.579%
[29 empty] | 2019 | June | 27 | 6 | 3931 | 28500 | 13.79%
[29 empty] | 2019 | June | 27 | 7 | 9586.5 | 28500 | 33.64%
[29 empty] | 2019 | June | 27 | 8 | 19662 | 28500 | 68.99%
[29 empty] | 2019 | June | 27 | 9 | 31359.5 | 28500 | 110%
[29 empty] | 2019 | June | 27 | 10 | 37223 | 28500 | 130.6%
[29 empty] | 2019 | June | 27 | 11 | 41182.5 | 28500 | 144.5%
[29 empty] | 2019 | June | 27 | 12 | 41454 | 28500 | 145.5%
[29 empty] | 2019 | June | 27 | 13 | 39492.5 | 28500 | 138.6%
[29 empty] | 2019 | June | 27 | 14 | 35299.5 | 28500 | 123.9%
[29 empty] | 2019 | June | 27 | 15 | 28475.5 | 28500 | 99.91%
[29 empty] | 2019 | June | 27 | 16 | 20010.5 | 28500 | 70.21%
[29 empty] | 2019 | June | 27 | 17 | 9174 | 28500 | 32.19%
[29 empty] | 2019 | June | 27 | 18 | 3706.5 | 28500 | 13.01%
[29 empty] | 2019 | June | 27 | 19 | 999 | 28500 | 3.505%
[29 empty] | 2019 | June | 27 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 27 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 27 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 27 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 28 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 28 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 28 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 28 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 28 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 28 | 5 | 1011.5 | 28500 | 3.549%
[29 empty] | 2019 | June | 28 | 6 | 4191.5 | 28500 | 14.71%
[29 empty] | 2019 | June | 28 | 7 | 9429 | 28500 | 33.08%
[29 empty] | 2019 | June | 28 | 8 | 17250.5 | 28500 | 60.53%
[29 empty] | 2019 | June | 28 | 9 | 28476.5 | 28500 | 99.92%
[29 empty] | 2019 | June | 28 | 10 | 35998 | 28500 | 126.3%
[29 empty] | 2019 | June | 28 | 11 | 39701.5 | 28500 | 139.3%
[29 empty] | 2019 | June | 28 | 12 | 41051 | 28500 | 144%
[29 empty] | 2019 | June | 28 | 13 | 39020.5 | 28500 | 136.9%
[29 empty] | 2019 | June | 28 | 14 | 34639 | 28500 | 121.5%
[29 empty] | 2019 | June | 28 | 15 | 28420.5 | 28500 | 99.72%
[29 empty] | 2019 | June | 28 | 16 | 19857 | 28500 | 69.67%
[29 empty] | 2019 | June | 28 | 17 | 9704.5 | 28500 | 34.05%
[29 empty] | 2019 | June | 28 | 18 | 2687.5 | 28500 | 9.43%
[29 empty] | 2019 | June | 28 | 19 | 1177.5 | 28500 | 4.132%
[29 empty] | 2019 | June | 28 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 28 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 28 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 28 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 29 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 29 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 29 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 29 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 29 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 29 | 5 | 1580 | 28500 | 5.544%
[29 empty] | 2019 | June | 29 | 6 | 4904.5 | 28500 | 17.21%
[29 empty] | 2019 | June | 29 | 7 | 12697.5 | 28500 | 44.55%
[29 empty] | 2019 | June | 29 | 8 | 22057 | 28500 | 77.39%
[29 empty] | 2019 | June | 29 | 9 | 29212.5 | 28500 | 102.5%
[29 empty] | 2019 | June | 29 | 10 | 35049.5 | 28500 | 123%
[29 empty] | 2019 | June | 29 | 11 | 37824 | 28500 | 132.7%
[29 empty] | 2019 | June | 29 | 12 | 39040 | 28500 | 137%
[29 empty] | 2019 | June | 29 | 13 | 37041.5 | 28500 | 130%
[29 empty] | 2019 | June | 29 | 14 | 32782 | 28500 | 115%
[29 empty] | 2019 | June | 29 | 15 | 27085.5 | 28500 | 95.04%
[29 empty] | 2019 | June | 29 | 16 | 19034 | 28500 | 66.79%
[29 empty] | 2019 | June | 29 | 17 | 9598.5 | 28500 | 33.68%
[29 empty] | 2019 | June | 29 | 18 | 2743.5 | 28500 | 9.626%
[29 empty] | 2019 | June | 29 | 19 | 1061 | 28500 | 3.723%
[29 empty] | 2019 | June | 29 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 29 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 29 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 29 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 30 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 30 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 30 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 30 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 30 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 30 | 5 | 1545.5 | 28500 | 5.423%
[29 empty] | 2019 | June | 30 | 6 | 3814.5 | 28500 | 13.38%
[29 empty] | 2019 | June | 30 | 7 | 12810.5 | 28500 | 44.95%
[29 empty] | 2019 | June | 30 | 8 | 21951 | 28500 | 77.02%
[29 empty] | 2019 | June | 30 | 9 | 25243.5 | 28500 | 88.57%
[29 empty] | 2019 | June | 30 | 10 | 34436 | 28500 | 120.8%
[29 empty] | 2019 | June | 30 | 11 | 38420 | 28500 | 134.8%
[29 empty] | 2019 | June | 30 | 12 | 33286.5 | 28500 | 116.8%
[29 empty] | 2019 | June | 30 | 13 | 36522.5 | 28500 | 128.1%
[29 empty] | 2019 | June | 30 | 14 | 24359 | 28500 | 85.47%
[29 empty] | 2019 | June | 30 | 15 | 21728.5 | 28500 | 76.24%
[29 empty] | 2019 | June | 30 | 16 | 16040 | 28500 | 56.28%
[29 empty] | 2019 | June | 30 | 17 | 9789 | 28500 | 34.35%
[29 empty] | 2019 | June | 30 | 18 | 3537 | 28500 | 12.41%
[29 empty] | 2019 | June | 30 | 19 | 1223 | 28500 | 4.291%
[29 empty] | 2019 | June | 30 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 30 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 30 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | June | 30 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 1 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 1 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 1 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 1 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 1 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 1 | 5 | 1395.5 | 28500 | 4.896%
[29 empty] | 2019 | July | 1 | 6 | 3742.5 | 28500 | 13.13%
[29 empty] | 2019 | July | 1 | 7 | 12189 | 28500 | 42.77%
[29 empty] | 2019 | July | 1 | 8 | 16988 | 28500 | 59.61%
[29 empty] | 2019 | July | 1 | 9 | 30112 | 28500 | 105.7%
[29 empty] | 2019 | July | 1 | 10 | 34341.5 | 28500 | 120.5%
[29 empty] | 2019 | July | 1 | 11 | 35460.5 | 28500 | 124.4%
[29 empty] | 2019 | July | 1 | 12 | 39815 | 28500 | 139.7%
[29 empty] | 2019 | July | 1 | 13 | 37978.5 | 28500 | 133.3%
[29 empty] | 2019 | July | 1 | 14 | 34329 | 28500 | 120.5%
[29 empty] | 2019 | July | 1 | 15 | 23375.5 | 28500 | 82.02%
[29 empty] | 2019 | July | 1 | 16 | 7172.5 | 28500 | 25.17%
[29 empty] | 2019 | July | 1 | 17 | 4719 | 28500 | 16.56%
[29 empty] | 2019 | July | 1 | 18 | 3200.5 | 28500 | 11.23%
[29 empty] | 2019 | July | 1 | 19 | 951.5 | 28500 | 3.339%
[29 empty] | 2019 | July | 1 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 1 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 1 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 1 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 2 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 2 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 2 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 2 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 2 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 2 | 5 | 1411 | 28500 | 4.951%
[29 empty] | 2019 | July | 2 | 6 | 3685.5 | 28500 | 12.93%
[29 empty] | 2019 | July | 2 | 7 | 13025 | 28500 | 45.7%
[29 empty] | 2019 | July | 2 | 8 | 22921.5 | 28500 | 80.43%
[29 empty] | 2019 | July | 2 | 9 | 28878 | 28500 | 101.3%
[29 empty] | 2019 | July | 2 | 10 | 18930 | 28500 | 66.42%
[29 empty] | 2019 | July | 2 | 11 | 22297 | 28500 | 78.24%
[29 empty] | 2019 | July | 2 | 12 | 22982 | 28500 | 80.64%
[29 empty] | 2019 | July | 2 | 13 | 16120 | 28500 | 56.56%
[29 empty] | 2019 | July | 2 | 14 | 19867 | 28500 | 69.71%
[29 empty] | 2019 | July | 2 | 15 | 15726.5 | 28500 | 55.18%
[29 empty] | 2019 | July | 2 | 16 | 9944.5 | 28500 | 34.89%
[29 empty] | 2019 | July | 2 | 17 | 8854.5 | 28500 | 31.07%
[29 empty] | 2019 | July | 2 | 18 | 3782.5 | 28500 | 13.27%
[29 empty] | 2019 | July | 2 | 19 | 1017 | 28500 | 3.568%
[29 empty] | 2019 | July | 2 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 2 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 2 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 2 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 3 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 3 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 3 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 3 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 3 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 3 | 5 | 1803.5 | 28500 | 6.328%
[29 empty] | 2019 | July | 3 | 6 | 3762.5 | 28500 | 13.2%
[29 empty] | 2019 | July | 3 | 7 | 12690 | 28500 | 44.53%
[29 empty] | 2019 | July | 3 | 8 | 22399 | 28500 | 78.59%
[29 empty] | 2019 | July | 3 | 9 | 23474.5 | 28500 | 82.37%
[29 empty] | 2019 | July | 3 | 10 | 27910 | 28500 | 97.93%
[29 empty] | 2019 | July | 3 | 11 | 28690.5 | 28500 | 100.7%
[29 empty] | 2019 | July | 3 | 12 | 21585.5 | 28500 | 75.74%
[29 empty] | 2019 | July | 3 | 13 | 20342.5 | 28500 | 71.38%
[29 empty] | 2019 | July | 3 | 14 | 27885.5 | 28500 | 97.84%
[29 empty] | 2019 | July | 3 | 15 | 26650.5 | 28500 | 93.51%
[29 empty] | 2019 | July | 3 | 16 | 20415.5 | 28500 | 71.63%
[29 empty] | 2019 | July | 3 | 17 | 10213 | 28500 | 35.84%
[29 empty] | 2019 | July | 3 | 18 | 2196.5 | 28500 | 7.707%
[29 empty] | 2019 | July | 3 | 19 | 867.5 | 28500 | 3.044%
[29 empty] | 2019 | July | 3 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 3 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 3 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 3 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 4 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 4 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 4 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 4 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 4 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 4 | 5 | 1349.5 | 28500 | 4.735%
[29 empty] | 2019 | July | 4 | 6 | 3450 | 28500 | 12.11%
[29 empty] | 2019 | July | 4 | 7 | 12752 | 28500 | 44.74%
[29 empty] | 2019 | July | 4 | 8 | 22727.5 | 28500 | 79.75%
[29 empty] | 2019 | July | 4 | 9 | 30638.5 | 28500 | 107.5%
[29 empty] | 2019 | July | 4 | 10 | 35629 | 28500 | 125%
[29 empty] | 2019 | July | 4 | 11 | 37651.5 | 28500 | 132.1%
[29 empty] | 2019 | July | 4 | 12 | 37903 | 28500 | 133%
[29 empty] | 2019 | July | 4 | 13 | 37149.5 | 28500 | 130.3%
[29 empty] | 2019 | July | 4 | 14 | 32847 | 28500 | 115.3%
[29 empty] | 2019 | July | 4 | 15 | 27196 | 28500 | 95.42%
[29 empty] | 2019 | July | 4 | 16 | 17795.5 | 28500 | 62.44%
[29 empty] | 2019 | July | 4 | 17 | 9606 | 28500 | 33.71%
[29 empty] | 2019 | July | 4 | 18 | 3639 | 28500 | 12.77%
[29 empty] | 2019 | July | 4 | 19 | 449 | 28500 | 1.575%
[29 empty] | 2019 | July | 4 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 4 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 4 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 4 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 5 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 5 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 5 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 5 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 5 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 5 | 5 | 1518.5 | 28500 | 5.328%
[29 empty] | 2019 | July | 5 | 6 | 4341 | 28500 | 15.23%
[29 empty] | 2019 | July | 5 | 7 | 12404.5 | 28500 | 43.52%
[29 empty] | 2019 | July | 5 | 8 | 21425.5 | 28500 | 75.18%
[29 empty] | 2019 | July | 5 | 9 | 29196 | 28500 | 102.4%
[29 empty] | 2019 | July | 5 | 10 | 34378 | 28500 | 120.6%
[29 empty] | 2019 | July | 5 | 11 | 32139 | 28500 | 112.8%
[29 empty] | 2019 | July | 5 | 12 | 38504 | 28500 | 135.1%
[29 empty] | 2019 | July | 5 | 13 | 33001 | 28500 | 115.8%
[29 empty] | 2019 | July | 5 | 14 | 33635.5 | 28500 | 118%
[29 empty] | 2019 | July | 5 | 15 | 27325 | 28500 | 95.88%
[29 empty] | 2019 | July | 5 | 16 | 13566 | 28500 | 47.6%
[29 empty] | 2019 | July | 5 | 17 | 5732.5 | 28500 | 20.11%
[29 empty] | 2019 | July | 5 | 18 | 2784 | 28500 | 9.768%
[29 empty] | 2019 | July | 5 | 19 | 961.5 | 28500 | 3.374%
[29 empty] | 2019 | July | 5 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 5 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 5 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 5 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 6 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 6 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 6 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 6 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 6 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 6 | 5 | 1683 | 28500 | 5.905%
[29 empty] | 2019 | July | 6 | 6 | 3367.5 | 28500 | 11.82%
[29 empty] | 2019 | July | 6 | 7 | 12134 | 28500 | 42.58%
[29 empty] | 2019 | July | 6 | 8 | 21913 | 28500 | 76.89%
[29 empty] | 2019 | July | 6 | 9 | 28352.5 | 28500 | 99.48%
[29 empty] | 2019 | July | 6 | 10 | 29297.5 | 28500 | 102.8%
[29 empty] | 2019 | July | 6 | 11 | 7469 | 28500 | 26.21%
[29 empty] | 2019 | July | 6 | 12 | 22799 | 28500 | 80%
[29 empty] | 2019 | July | 6 | 13 | 13378.5 | 28500 | 46.94%
[29 empty] | 2019 | July | 6 | 14 | 16279 | 28500 | 57.12%
[29 empty] | 2019 | July | 6 | 15 | 18467 | 28500 | 64.8%
[29 empty] | 2019 | July | 6 | 16 | 3138.5 | 28500 | 11.01%
[29 empty] | 2019 | July | 6 | 17 | 4550.5 | 28500 | 15.97%
[29 empty] | 2019 | July | 6 | 18 | 1396.5 | 28500 | 4.9%
[29 empty] | 2019 | July | 6 | 19 | 18 | 28500 | 0.06316%
[29 empty] | 2019 | July | 6 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 6 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 6 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 6 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 7 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 7 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 7 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 7 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 7 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 7 | 5 | 183 | 28500 | 0.6421%
[29 empty] | 2019 | July | 7 | 6 | 911 | 28500 | 3.196%
[29 empty] | 2019 | July | 7 | 7 | 3378.5 | 28500 | 11.85%
[29 empty] | 2019 | July | 7 | 8 | 5682.5 | 28500 | 19.94%
[29 empty] | 2019 | July | 7 | 9 | 6452.5 | 28500 | 22.64%
[29 empty] | 2019 | July | 7 | 10 | 5627 | 28500 | 19.74%
[29 empty] | 2019 | July | 7 | 11 | 9399.5 | 28500 | 32.98%
[29 empty] | 2019 | July | 7 | 12 | 3738 | 28500 | 13.12%
[29 empty] | 2019 | July | 7 | 13 | 10183.5 | 28500 | 35.73%
[29 empty] | 2019 | July | 7 | 14 | 23316 | 28500 | 81.81%
[29 empty] | 2019 | July | 7 | 15 | 23154 | 28500 | 81.24%
[29 empty] | 2019 | July | 7 | 16 | 18072.5 | 28500 | 63.41%
[29 empty] | 2019 | July | 7 | 17 | 8459.5 | 28500 | 29.68%
[29 empty] | 2019 | July | 7 | 18 | 3034 | 28500 | 10.65%
[29 empty] | 2019 | July | 7 | 19 | 228 | 28500 | 0.8%
[29 empty] | 2019 | July | 7 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 7 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 7 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 7 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 8 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 8 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 8 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 8 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 8 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 8 | 5 | 140.5 | 28500 | 0.493%
[29 empty] | 2019 | July | 8 | 6 | 3634 | 28500 | 12.75%
[29 empty] | 2019 | July | 8 | 7 | 10732.5 | 28500 | 37.66%
[29 empty] | 2019 | July | 8 | 8 | 18181.5 | 28500 | 63.79%
[29 empty] | 2019 | July | 8 | 9 | 23460 | 28500 | 82.32%
[29 empty] | 2019 | July | 8 | 10 | 21470.5 | 28500 | 75.34%
[29 empty] | 2019 | July | 8 | 11 | 22340.5 | 28500 | 78.39%
[29 empty] | 2019 | July | 8 | 12 | 24900 | 28500 | 87.37%
[29 empty] | 2019 | July | 8 | 13 | 20685.5 | 28500 | 72.58%
[29 empty] | 2019 | July | 8 | 14 | 22349 | 28500 | 78.42%
[29 empty] | 2019 | July | 8 | 15 | 21978 | 28500 | 77.12%
[29 empty] | 2019 | July | 8 | 16 | 12246.5 | 28500 | 42.97%
[29 empty] | 2019 | July | 8 | 17 | 7001.5 | 28500 | 24.57%
[29 empty] | 2019 | July | 8 | 18 | 3013.5 | 28500 | 10.57%
[29 empty] | 2019 | July | 8 | 19 | 203 | 28500 | 0.7123%
[29 empty] | 2019 | July | 8 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 8 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 8 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 8 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 9 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 9 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 9 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 9 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 9 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 9 | 5 | 184.5 | 28500 | 0.6474%
[29 empty] | 2019 | July | 9 | 6 | 1856 | 28500 | 6.512%
[29 empty] | 2019 | July | 9 | 7 | 4626 | 28500 | 16.23%
[29 empty] | 2019 | July | 9 | 8 | 6987 | 28500 | 24.52%
[29 empty] | 2019 | July | 9 | 9 | 12707.5 | 28500 | 44.59%
[29 empty] | 2019 | July | 9 | 10 | 14581 | 28500 | 51.16%
[29 empty] | 2019 | July | 9 | 11 | 30249.5 | 28500 | 106.1%
[29 empty] | 2019 | July | 9 | 12 | 18919.5 | 28500 | 66.38%
[29 empty] | 2019 | July | 9 | 13 | 5266.5 | 28500 | 18.48%
[29 empty] | 2019 | July | 9 | 14 | 31781.5 | 28500 | 111.5%
[29 empty] | 2019 | July | 9 | 15 | 12687 | 28500 | 44.52%
[29 empty] | 2019 | July | 9 | 16 | 8618 | 28500 | 30.24%
[29 empty] | 2019 | July | 9 | 17 | 5907.5 | 28500 | 20.73%
[29 empty] | 2019 | July | 9 | 18 | 2911.5 | 28500 | 10.22%
[29 empty] | 2019 | July | 9 | 19 | 947 | 28500 | 3.323%
[29 empty] | 2019 | July | 9 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 9 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 9 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 9 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 10 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 10 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 10 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 10 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 10 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 10 | 5 | 636 | 28500 | 2.232%
[29 empty] | 2019 | July | 10 | 6 | 4404.5 | 28500 | 15.45%
[29 empty] | 2019 | July | 10 | 7 | 7609 | 28500 | 26.7%
[29 empty] | 2019 | July | 10 | 8 | 14039.5 | 28500 | 49.26%
[29 empty] | 2019 | July | 10 | 9 | 15894.5 | 28500 | 55.77%
[29 empty] | 2019 | July | 10 | 10 | 9370 | 28500 | 32.88%
[29 empty] | 2019 | July | 10 | 11 | 15218 | 28500 | 53.4%
[29 empty] | 2019 | July | 10 | 12 | 22999.5 | 28500 | 80.7%
[29 empty] | 2019 | July | 10 | 13 | 22825.5 | 28500 | 80.09%
[29 empty] | 2019 | July | 10 | 14 | 18206 | 28500 | 63.88%
[29 empty] | 2019 | July | 10 | 15 | 16416.5 | 28500 | 57.6%
[29 empty] | 2019 | July | 10 | 16 | 16261 | 28500 | 57.06%
[29 empty] | 2019 | July | 10 | 17 | 9593.5 | 28500 | 33.66%
[29 empty] | 2019 | July | 10 | 18 | 2095 | 28500 | 7.351%
[29 empty] | 2019 | July | 10 | 19 | 1002 | 28500 | 3.516%
[29 empty] | 2019 | July | 10 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 10 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 10 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 10 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 11 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 11 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 11 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 11 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 11 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 11 | 5 | 331.5 | 28500 | 1.163%
[29 empty] | 2019 | July | 11 | 6 | 3475.5 | 28500 | 12.19%
[29 empty] | 2019 | July | 11 | 7 | 9894 | 28500 | 34.72%
[29 empty] | 2019 | July | 11 | 8 | 13544.5 | 28500 | 47.52%
[29 empty] | 2019 | July | 11 | 9 | 22822 | 28500 | 80.08%
[29 empty] | 2019 | July | 11 | 10 | 30223 | 28500 | 106%
[29 empty] | 2019 | July | 11 | 11 | 37067.5 | 28500 | 130.1%
[29 empty] | 2019 | July | 11 | 12 | 36836.5 | 28500 | 129.3%
[29 empty] | 2019 | July | 11 | 13 | 32283.5 | 28500 | 113.3%
[29 empty] | 2019 | July | 11 | 14 | 28143 | 28500 | 98.75%
[29 empty] | 2019 | July | 11 | 15 | 19140.5 | 28500 | 67.16%
[29 empty] | 2019 | July | 11 | 16 | 18838.5 | 28500 | 66.1%
[29 empty] | 2019 | July | 11 | 17 | 9430.5 | 28500 | 33.09%
[29 empty] | 2019 | July | 11 | 18 | 3118 | 28500 | 10.94%
[29 empty] | 2019 | July | 11 | 19 | 476.5 | 28500 | 1.672%
[29 empty] | 2019 | July | 11 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 11 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 11 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 11 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 12 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 12 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 12 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 12 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 12 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 12 | 5 | 874.5 | 28500 | 3.068%
[29 empty] | 2019 | July | 12 | 6 | 4367 | 28500 | 15.32%
[29 empty] | 2019 | July | 12 | 7 | 11998 | 28500 | 42.1%
[29 empty] | 2019 | July | 12 | 8 | 21567.5 | 28500 | 75.68%
[29 empty] | 2019 | July | 12 | 9 | 20583 | 28500 | 72.22%
[29 empty] | 2019 | July | 12 | 10 | 20725 | 28500 | 72.72%
[29 empty] | 2019 | July | 12 | 11 | 28323 | 28500 | 99.38%
[29 empty] | 2019 | July | 12 | 12 | 34756.5 | 28500 | 122%
[29 empty] | 2019 | July | 12 | 13 | 9940 | 28500 | 34.88%
[29 empty] | 2019 | July | 12 | 14 | 15905 | 28500 | 55.81%
[29 empty] | 2019 | July | 12 | 15 | 11324.5 | 28500 | 39.74%
[29 empty] | 2019 | July | 12 | 16 | 16493.5 | 28500 | 57.87%
[29 empty] | 2019 | July | 12 | 17 | 9996 | 28500 | 35.07%
[29 empty] | 2019 | July | 12 | 18 | 2599.5 | 28500 | 9.121%
[29 empty] | 2019 | July | 12 | 19 | 822.5 | 28500 | 2.886%
[29 empty] | 2019 | July | 12 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 12 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 12 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 12 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 13 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 13 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 13 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 13 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 13 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 13 | 5 | 1327.5 | 28500 | 4.658%
[29 empty] | 2019 | July | 13 | 6 | 4426 | 28500 | 15.53%
[29 empty] | 2019 | July | 13 | 7 | 10638 | 28500 | 37.33%
[29 empty] | 2019 | July | 13 | 8 | 14808.5 | 28500 | 51.96%
[29 empty] | 2019 | July | 13 | 9 | 25628 | 28500 | 89.92%
[29 empty] | 2019 | July | 13 | 10 | 16811 | 28500 | 58.99%
[29 empty] | 2019 | July | 13 | 11 | 14411.5 | 28500 | 50.57%
[29 empty] | 2019 | July | 13 | 12 | 14742 | 28500 | 51.73%
[29 empty] | 2019 | July | 13 | 13 | 15156 | 28500 | 53.18%
[29 empty] | 2019 | July | 13 | 14 | 13228.5 | 28500 | 46.42%
[29 empty] | 2019 | July | 13 | 15 | 15361 | 28500 | 53.9%
[29 empty] | 2019 | July | 13 | 16 | 11928 | 28500 | 41.85%
[29 empty] | 2019 | July | 13 | 17 | 8837.5 | 28500 | 31.01%
[29 empty] | 2019 | July | 13 | 18 | 3323 | 28500 | 11.66%
[29 empty] | 2019 | July | 13 | 19 | 402.5 | 28500 | 1.412%
[29 empty] | 2019 | July | 13 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 13 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 13 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 13 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 14 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 14 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 14 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 14 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 14 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 14 | 5 | 1424.5 | 28500 | 4.998%
[29 empty] | 2019 | July | 14 | 6 | 3788 | 28500 | 13.29%
[29 empty] | 2019 | July | 14 | 7 | 6898 | 28500 | 24.2%
[29 empty] | 2019 | July | 14 | 8 | 6850 | 28500 | 24.04%
[29 empty] | 2019 | July | 14 | 9 | 21491 | 28500 | 75.41%
[29 empty] | 2019 | July | 14 | 10 | 15315.5 | 28500 | 53.74%
[29 empty] | 2019 | July | 14 | 11 | 19436.5 | 28500 | 68.2%
[29 empty] | 2019 | July | 14 | 12 | 26774.5 | 28500 | 93.95%
[29 empty] | 2019 | July | 14 | 13 | 10927.5 | 28500 | 38.34%
[29 empty] | 2019 | July | 14 | 14 | 8613.5 | 28500 | 30.22%
[29 empty] | 2019 | July | 14 | 15 | 22468.5 | 28500 | 78.84%
[29 empty] | 2019 | July | 14 | 16 | 9225 | 28500 | 32.37%
[29 empty] | 2019 | July | 14 | 17 | 10080 | 28500 | 35.37%
[29 empty] | 2019 | July | 14 | 18 | 2192 | 28500 | 7.691%
[29 empty] | 2019 | July | 14 | 19 | 571.5 | 28500 | 2.005%
[29 empty] | 2019 | July | 14 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 14 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 14 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 14 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 15 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 15 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 15 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 15 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 15 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 15 | 5 | 706 | 28500 | 2.477%
[29 empty] | 2019 | July | 15 | 6 | 3257.5 | 28500 | 11.43%
[29 empty] | 2019 | July | 15 | 7 | 5144.5 | 28500 | 18.05%
[29 empty] | 2019 | July | 15 | 8 | 5840 | 28500 | 20.49%
[29 empty] | 2019 | July | 15 | 9 | 8302.5 | 28500 | 29.13%
[29 empty] | 2019 | July | 15 | 10 | 12724.5 | 28500 | 44.65%
[29 empty] | 2019 | July | 15 | 11 | 21193 | 28500 | 74.36%
[29 empty] | 2019 | July | 15 | 12 | 17704 | 28500 | 62.12%
[29 empty] | 2019 | July | 15 | 13 | 15243 | 28500 | 53.48%
[29 empty] | 2019 | July | 15 | 14 | 15814.5 | 28500 | 55.49%
[29 empty] | 2019 | July | 15 | 15 | 23659 | 28500 | 83.01%
[29 empty] | 2019 | July | 15 | 16 | 18791 | 28500 | 65.93%
[29 empty] | 2019 | July | 15 | 17 | 9834.5 | 28500 | 34.51%
[29 empty] | 2019 | July | 15 | 18 | 3140 | 28500 | 11.02%
[29 empty] | 2019 | July | 15 | 19 | 831.5 | 28500 | 2.918%
[29 empty] | 2019 | July | 15 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 15 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 15 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 15 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 16 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 16 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 16 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 16 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 16 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 16 | 5 | 1405 | 28500 | 4.93%
[29 empty] | 2019 | July | 16 | 6 | 4096.5 | 28500 | 14.37%
[29 empty] | 2019 | July | 16 | 7 | 11748 | 28500 | 41.22%
[29 empty] | 2019 | July | 16 | 8 | 21976 | 28500 | 77.11%
[29 empty] | 2019 | July | 16 | 9 | 29433.5 | 28500 | 103.3%
[29 empty] | 2019 | July | 16 | 10 | 34182.5 | 28500 | 119.9%
[29 empty] | 2019 | July | 16 | 11 | 34474.5 | 28500 | 121%
[29 empty] | 2019 | July | 16 | 12 | 34168 | 28500 | 119.9%
[29 empty] | 2019 | July | 16 | 13 | 29533.5 | 28500 | 103.6%
[29 empty] | 2019 | July | 16 | 14 | 27254.5 | 28500 | 95.63%
[29 empty] | 2019 | July | 16 | 15 | 21797 | 28500 | 76.48%
[29 empty] | 2019 | July | 16 | 16 | 18013 | 28500 | 63.2%
[29 empty] | 2019 | July | 16 | 17 | 10038.5 | 28500 | 35.22%
[29 empty] | 2019 | July | 16 | 18 | 2181 | 28500 | 7.653%
[29 empty] | 2019 | July | 16 | 19 | 940 | 28500 | 3.298%
[29 empty] | 2019 | July | 16 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 16 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 16 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 16 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 17 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 17 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 17 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 17 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 17 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 17 | 5 | 1367.5 | 28500 | 4.798%
[29 empty] | 2019 | July | 17 | 6 | 4021.5 | 28500 | 14.11%
[29 empty] | 2019 | July | 17 | 7 | 10684 | 28500 | 37.49%
[29 empty] | 2019 | July | 17 | 8 | 19194 | 28500 | 67.35%
[29 empty] | 2019 | July | 17 | 9 | 27992 | 28500 | 98.22%
[29 empty] | 2019 | July | 17 | 10 | 29607.5 | 28500 | 103.9%
[29 empty] | 2019 | July | 17 | 11 | 32700 | 28500 | 114.7%
[29 empty] | 2019 | July | 17 | 12 | 27415 | 28500 | 96.19%
[29 empty] | 2019 | July | 17 | 13 | 21932 | 28500 | 76.95%
[29 empty] | 2019 | July | 17 | 14 | 19256 | 28500 | 67.56%
[29 empty] | 2019 | July | 17 | 15 | 7130.5 | 28500 | 25.02%
[29 empty] | 2019 | July | 17 | 16 | 9018 | 28500 | 31.64%
[29 empty] | 2019 | July | 17 | 17 | 2828 | 28500 | 9.923%
[29 empty] | 2019 | July | 17 | 18 | 1656 | 28500 | 5.811%
[29 empty] | 2019 | July | 17 | 19 | 2 | 28500 | 0.007018%
[29 empty] | 2019 | July | 17 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 17 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 17 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 17 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 18 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 18 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 18 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 18 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 18 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 18 | 5 | 54.5 | 28500 | 0.1912%
[29 empty] | 2019 | July | 18 | 6 | 2204.5 | 28500 | 7.735%
[29 empty] | 2019 | July | 18 | 7 | 2453 | 28500 | 8.607%
[29 empty] | 2019 | July | 18 | 8 | 2600 | 28500 | 9.123%
[29 empty] | 2019 | July | 18 | 9 | 5589.5 | 28500 | 19.61%
[29 empty] | 2019 | July | 18 | 10 | 11855.5 | 28500 | 41.6%
[29 empty] | 2019 | July | 18 | 11 | 6910 | 28500 | 24.25%
[29 empty] | 2019 | July | 18 | 12 | 6187 | 28500 | 21.71%
[29 empty] | 2019 | July | 18 | 13 | 10835 | 28500 | 38.02%
[29 empty] | 2019 | July | 18 | 14 | 9966.5 | 28500 | 34.97%
[29 empty] | 2019 | July | 18 | 15 | 17635.5 | 28500 | 61.88%
[29 empty] | 2019 | July | 18 | 16 | 13176.5 | 28500 | 46.23%
[29 empty] | 2019 | July | 18 | 17 | 8035.5 | 28500 | 28.19%
[29 empty] | 2019 | July | 18 | 18 | 3319 | 28500 | 11.65%
[29 empty] | 2019 | July | 18 | 19 | 823 | 28500 | 2.888%
[29 empty] | 2019 | July | 18 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 18 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 18 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 18 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 19 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 19 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 19 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 19 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 19 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 19 | 5 | 1069.5 | 28500 | 3.753%
[29 empty] | 2019 | July | 19 | 6 | 1076 | 28500 | 3.775%
[29 empty] | 2019 | July | 19 | 7 | 5542 | 28500 | 19.45%
[29 empty] | 2019 | July | 19 | 8 | 6516 | 28500 | 22.86%
[29 empty] | 2019 | July | 19 | 9 | 14796 | 28500 | 51.92%
[29 empty] | 2019 | July | 19 | 10 | 6799 | 28500 | 23.86%
[29 empty] | 2019 | July | 19 | 11 | 15923.5 | 28500 | 55.87%
[29 empty] | 2019 | July | 19 | 12 | 3709 | 28500 | 13.01%
[29 empty] | 2019 | July | 19 | 13 | 5334.5 | 28500 | 18.72%
[29 empty] | 2019 | July | 19 | 14 | 9847 | 28500 | 34.55%
[29 empty] | 2019 | July | 19 | 15 | 2942 | 28500 | 10.32%
[29 empty] | 2019 | July | 19 | 16 | 8954 | 28500 | 31.42%
[29 empty] | 2019 | July | 19 | 17 | 1565 | 28500 | 5.491%
[29 empty] | 2019 | July | 19 | 18 | 258.5 | 28500 | 0.907%
[29 empty] | 2019 | July | 19 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 19 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 19 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 19 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 19 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 20 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 20 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 20 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 20 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 20 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 20 | 5 | 1150 | 28500 | 4.035%
[29 empty] | 2019 | July | 20 | 6 | 3993 | 28500 | 14.01%
[29 empty] | 2019 | July | 20 | 7 | 1476.5 | 28500 | 5.181%
[29 empty] | 2019 | July | 20 | 8 | 10318 | 28500 | 36.2%
[29 empty] | 2019 | July | 20 | 9 | 22462 | 28500 | 78.81%
[29 empty] | 2019 | July | 20 | 10 | 32386.5 | 28500 | 113.6%
[29 empty] | 2019 | July | 20 | 11 | 8017 | 28500 | 28.13%
[29 empty] | 2019 | July | 20 | 12 | 35852 | 28500 | 125.8%
[29 empty] | 2019 | July | 20 | 13 | 15098.5 | 28500 | 52.98%
[29 empty] | 2019 | July | 20 | 14 | 23811.5 | 28500 | 83.55%
[29 empty] | 2019 | July | 20 | 15 | 18085.5 | 28500 | 63.46%
[29 empty] | 2019 | July | 20 | 16 | 17377.5 | 28500 | 60.97%
[29 empty] | 2019 | July | 20 | 17 | 6686 | 28500 | 23.46%
[29 empty] | 2019 | July | 20 | 18 | 3249.5 | 28500 | 11.4%
[29 empty] | 2019 | July | 20 | 19 | 855 | 28500 | 3%
[29 empty] | 2019 | July | 20 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 20 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 20 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 20 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 21 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 21 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 21 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 21 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 21 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 21 | 5 | 444.5 | 28500 | 1.56%
[29 empty] | 2019 | July | 21 | 6 | 4022 | 28500 | 14.11%
[29 empty] | 2019 | July | 21 | 7 | 10935.5 | 28500 | 38.37%
[29 empty] | 2019 | July | 21 | 8 | 21034.5 | 28500 | 73.81%
[29 empty] | 2019 | July | 21 | 9 | 28271.5 | 28500 | 99.2%
[29 empty] | 2019 | July | 21 | 10 | 14280 | 28500 | 50.11%
[29 empty] | 2019 | July | 21 | 11 | 13979.5 | 28500 | 49.05%
[29 empty] | 2019 | July | 21 | 12 | 22484 | 28500 | 78.89%
[29 empty] | 2019 | July | 21 | 13 | 27577.5 | 28500 | 96.76%
[29 empty] | 2019 | July | 21 | 14 | 25206 | 28500 | 88.44%
[29 empty] | 2019 | July | 21 | 15 | 15444.5 | 28500 | 54.19%
[29 empty] | 2019 | July | 21 | 16 | 10873 | 28500 | 38.15%
[29 empty] | 2019 | July | 21 | 17 | 6927.5 | 28500 | 24.31%
[29 empty] | 2019 | July | 21 | 18 | 3146 | 28500 | 11.04%
[29 empty] | 2019 | July | 21 | 19 | 654 | 28500 | 2.295%
[29 empty] | 2019 | July | 21 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 21 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 21 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 21 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 22 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 22 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 22 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 22 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 22 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 22 | 5 | 1094 | 28500 | 3.839%
[29 empty] | 2019 | July | 22 | 6 | 3055 | 28500 | 10.72%
[29 empty] | 2019 | July | 22 | 7 | 10130.5 | 28500 | 35.55%
[29 empty] | 2019 | July | 22 | 8 | 19421 | 28500 | 68.14%
[29 empty] | 2019 | July | 22 | 9 | 13777.5 | 28500 | 48.34%
[29 empty] | 2019 | July | 22 | 10 | 12011.5 | 28500 | 42.15%
[29 empty] | 2019 | July | 22 | 11 | 15335 | 28500 | 53.81%
[29 empty] | 2019 | July | 22 | 12 | 14631 | 28500 | 51.34%
[29 empty] | 2019 | July | 22 | 13 | 14102.5 | 28500 | 49.48%
[29 empty] | 2019 | July | 22 | 14 | 26883.5 | 28500 | 94.33%
[29 empty] | 2019 | July | 22 | 15 | 24906.5 | 28500 | 87.39%
[29 empty] | 2019 | July | 22 | 16 | 18833.5 | 28500 | 66.08%
[29 empty] | 2019 | July | 22 | 17 | 9414 | 28500 | 33.03%
[29 empty] | 2019 | July | 22 | 18 | 1830.5 | 28500 | 6.423%
[29 empty] | 2019 | July | 22 | 19 | 727.5 | 28500 | 2.553%
[29 empty] | 2019 | July | 22 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 22 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 22 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 22 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 23 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 23 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 23 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 23 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 23 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 23 | 5 | 1099 | 28500 | 3.856%
[29 empty] | 2019 | July | 23 | 6 | 3098 | 28500 | 10.87%
[29 empty] | 2019 | July | 23 | 7 | 11524 | 28500 | 40.44%
[29 empty] | 2019 | July | 23 | 8 | 21063 | 28500 | 73.91%
[29 empty] | 2019 | July | 23 | 9 | 28946 | 28500 | 101.6%
[29 empty] | 2019 | July | 23 | 10 | 33958.5 | 28500 | 119.2%
[29 empty] | 2019 | July | 23 | 11 | 36940.5 | 28500 | 129.6%
[29 empty] | 2019 | July | 23 | 12 | 37915.5 | 28500 | 133%
[29 empty] | 2019 | July | 23 | 13 | 36339.5 | 28500 | 127.5%
[29 empty] | 2019 | July | 23 | 14 | 32849 | 28500 | 115.3%
[29 empty] | 2019 | July | 23 | 15 | 26392 | 28500 | 92.6%
[29 empty] | 2019 | July | 23 | 16 | 18479.5 | 28500 | 64.84%
[29 empty] | 2019 | July | 23 | 17 | 9470.5 | 28500 | 33.23%
[29 empty] | 2019 | July | 23 | 18 | 2417 | 28500 | 8.481%
[29 empty] | 2019 | July | 23 | 19 | 712.5 | 28500 | 2.5%
[29 empty] | 2019 | July | 23 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 23 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 23 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 23 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 24 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 24 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 24 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 24 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 24 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 24 | 5 | 941.5 | 28500 | 3.304%
[29 empty] | 2019 | July | 24 | 6 | 3732 | 28500 | 13.09%
[29 empty] | 2019 | July | 24 | 7 | 11123 | 28500 | 39.03%
[29 empty] | 2019 | July | 24 | 8 | 20607.5 | 28500 | 72.31%
[29 empty] | 2019 | July | 24 | 9 | 28561.5 | 28500 | 100.2%
[29 empty] | 2019 | July | 24 | 10 | 33787.5 | 28500 | 118.6%
[29 empty] | 2019 | July | 24 | 11 | 36598.5 | 28500 | 128.4%
[29 empty] | 2019 | July | 24 | 12 | 37683 | 28500 | 132.2%
[29 empty] | 2019 | July | 24 | 13 | 34201 | 28500 | 120%
[29 empty] | 2019 | July | 24 | 14 | 32319.5 | 28500 | 113.4%
[29 empty] | 2019 | July | 24 | 15 | 26856 | 28500 | 94.23%
[29 empty] | 2019 | July | 24 | 16 | 18587.5 | 28500 | 65.22%
[29 empty] | 2019 | July | 24 | 17 | 9521.5 | 28500 | 33.41%
[29 empty] | 2019 | July | 24 | 18 | 2668 | 28500 | 9.361%
[29 empty] | 2019 | July | 24 | 19 | 631 | 28500 | 2.214%
[29 empty] | 2019 | July | 24 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 24 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 24 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 24 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 25 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 25 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 25 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 25 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 25 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 25 | 5 | 972 | 28500 | 3.411%
[29 empty] | 2019 | July | 25 | 6 | 3095 | 28500 | 10.86%
[29 empty] | 2019 | July | 25 | 7 | 10913.5 | 28500 | 38.29%
[29 empty] | 2019 | July | 25 | 8 | 20132.5 | 28500 | 70.64%
[29 empty] | 2019 | July | 25 | 9 | 27672.5 | 28500 | 97.1%
[29 empty] | 2019 | July | 25 | 10 | 32386 | 28500 | 113.6%
[29 empty] | 2019 | July | 25 | 11 | 34886.5 | 28500 | 122.4%
[29 empty] | 2019 | July | 25 | 12 | 36180.5 | 28500 | 126.9%
[29 empty] | 2019 | July | 25 | 13 | 17624 | 28500 | 61.84%
[29 empty] | 2019 | July | 25 | 14 | 6591.5 | 28500 | 23.13%
[29 empty] | 2019 | July | 25 | 15 | 20876.5 | 28500 | 73.25%
[29 empty] | 2019 | July | 25 | 16 | 10939 | 28500 | 38.38%
[29 empty] | 2019 | July | 25 | 17 | 2181 | 28500 | 7.653%
[29 empty] | 2019 | July | 25 | 18 | 213 | 28500 | 0.7474%
[29 empty] | 2019 | July | 25 | 19 | 14 | 28500 | 0.04912%
[29 empty] | 2019 | July | 25 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 25 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 25 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 25 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 26 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 26 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 26 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 26 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 26 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 26 | 5 | 826 | 28500 | 2.898%
[29 empty] | 2019 | July | 26 | 6 | 788 | 28500 | 2.765%
[29 empty] | 2019 | July | 26 | 7 | 2042.5 | 28500 | 7.167%
[29 empty] | 2019 | July | 26 | 8 | 1137.5 | 28500 | 3.991%
[29 empty] | 2019 | July | 26 | 9 | 13440 | 28500 | 47.16%
[29 empty] | 2019 | July | 26 | 10 | 1834 | 28500 | 6.435%
[29 empty] | 2019 | July | 26 | 11 | 3905.5 | 28500 | 13.7%
[29 empty] | 2019 | July | 26 | 12 | 3080 | 28500 | 10.81%
[29 empty] | 2019 | July | 26 | 13 | 18524.5 | 28500 | 65%
[29 empty] | 2019 | July | 26 | 14 | 20526.5 | 28500 | 72.02%
[29 empty] | 2019 | July | 26 | 15 | 18103.5 | 28500 | 63.52%
[29 empty] | 2019 | July | 26 | 16 | 12998 | 28500 | 45.61%
[29 empty] | 2019 | July | 26 | 17 | 2915 | 28500 | 10.23%
[29 empty] | 2019 | July | 26 | 18 | 685 | 28500 | 2.404%
[29 empty] | 2019 | July | 26 | 19 | 368.5 | 28500 | 1.293%
[29 empty] | 2019 | July | 26 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 26 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 26 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 26 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 27 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 27 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 27 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 27 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 27 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 27 | 5 | 18.5 | 28500 | 0.06491%
[29 empty] | 2019 | July | 27 | 6 | 1616.5 | 28500 | 5.672%
[29 empty] | 2019 | July | 27 | 7 | 1134 | 28500 | 3.979%
[29 empty] | 2019 | July | 27 | 8 | 1723.5 | 28500 | 6.047%
[29 empty] | 2019 | July | 27 | 9 | 2444 | 28500 | 8.575%
[29 empty] | 2019 | July | 27 | 10 | 4811.5 | 28500 | 16.88%
[29 empty] | 2019 | July | 27 | 11 | 4696 | 28500 | 16.48%
[29 empty] | 2019 | July | 27 | 12 | 6383 | 28500 | 22.4%
[29 empty] | 2019 | July | 27 | 13 | 7481.5 | 28500 | 26.25%
[29 empty] | 2019 | July | 27 | 14 | 3393 | 28500 | 11.91%
[29 empty] | 2019 | July | 27 | 15 | 6043 | 28500 | 21.2%
[29 empty] | 2019 | July | 27 | 16 | 2946.5 | 28500 | 10.34%
[29 empty] | 2019 | July | 27 | 17 | 3320.5 | 28500 | 11.65%
[29 empty] | 2019 | July | 27 | 18 | 1127.5 | 28500 | 3.956%
[29 empty] | 2019 | July | 27 | 19 | 35.5 | 28500 | 0.1246%
[29 empty] | 2019 | July | 27 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 27 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 27 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 27 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 28 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 28 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 28 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 28 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 28 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 28 | 5 | 94.5 | 28500 | 0.3316%
[29 empty] | 2019 | July | 28 | 6 | 1247 | 28500 | 4.375%
[29 empty] | 2019 | July | 28 | 7 | 3443 | 28500 | 12.08%
[29 empty] | 2019 | July | 28 | 8 | 5317 | 28500 | 18.66%
[29 empty] | 2019 | July | 28 | 9 | 7164.5 | 28500 | 25.14%
[29 empty] | 2019 | July | 28 | 10 | 5870 | 28500 | 20.6%
[29 empty] | 2019 | July | 28 | 11 | 9020 | 28500 | 31.65%
[29 empty] | 2019 | July | 28 | 12 | 11457.5 | 28500 | 40.2%
[29 empty] | 2019 | July | 28 | 13 | 24486.5 | 28500 | 85.92%
[29 empty] | 2019 | July | 28 | 14 | 21972.5 | 28500 | 77.1%
[29 empty] | 2019 | July | 28 | 15 | 7882 | 28500 | 27.66%
[29 empty] | 2019 | July | 28 | 16 | 9248 | 28500 | 32.45%
[29 empty] | 2019 | July | 28 | 17 | 7627 | 28500 | 26.76%
[29 empty] | 2019 | July | 28 | 18 | 2734.5 | 28500 | 9.595%
[29 empty] | 2019 | July | 28 | 19 | 482 | 28500 | 1.691%
[29 empty] | 2019 | July | 28 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 28 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 28 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 28 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 29 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 29 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 29 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 29 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 29 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 29 | 5 | 825 | 28500 | 2.895%
[29 empty] | 2019 | July | 29 | 6 | 2742.5 | 28500 | 9.623%
[29 empty] | 2019 | July | 29 | 7 | 11565.5 | 28500 | 40.58%
[29 empty] | 2019 | July | 29 | 8 | 21206 | 28500 | 74.41%
[29 empty] | 2019 | July | 29 | 9 | 29129.5 | 28500 | 102.2%
[29 empty] | 2019 | July | 29 | 10 | 34371.5 | 28500 | 120.6%
[29 empty] | 2019 | July | 29 | 11 | 37077 | 28500 | 130.1%
[29 empty] | 2019 | July | 29 | 12 | 33278 | 28500 | 116.8%
[29 empty] | 2019 | July | 29 | 13 | 35267.5 | 28500 | 123.7%
[29 empty] | 2019 | July | 29 | 14 | 34289 | 28500 | 120.3%
[29 empty] | 2019 | July | 29 | 15 | 26796.5 | 28500 | 94.02%
[29 empty] | 2019 | July | 29 | 16 | 14698.5 | 28500 | 51.57%
[29 empty] | 2019 | July | 29 | 17 | 9597 | 28500 | 33.67%
[29 empty] | 2019 | July | 29 | 18 | 2545.5 | 28500 | 8.932%
[29 empty] | 2019 | July | 29 | 19 | 560 | 28500 | 1.965%
[29 empty] | 2019 | July | 29 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 29 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 29 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 29 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 30 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 30 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 30 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 30 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 30 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 30 | 5 | 811 | 28500 | 2.846%
[29 empty] | 2019 | July | 30 | 6 | 3430 | 28500 | 12.04%
[29 empty] | 2019 | July | 30 | 7 | 7539 | 28500 | 26.45%
[29 empty] | 2019 | July | 30 | 8 | 5496 | 28500 | 19.28%
[29 empty] | 2019 | July | 30 | 9 | 3769.5 | 28500 | 13.23%
[29 empty] | 2019 | July | 30 | 10 | 3739 | 28500 | 13.12%
[29 empty] | 2019 | July | 30 | 11 | 3095 | 28500 | 10.86%
[29 empty] | 2019 | July | 30 | 12 | 5749 | 28500 | 20.17%
[29 empty] | 2019 | July | 30 | 13 | 4916.5 | 28500 | 17.25%
[29 empty] | 2019 | July | 30 | 14 | 8026 | 28500 | 28.16%
[29 empty] | 2019 | July | 30 | 15 | 5885.5 | 28500 | 20.65%
[29 empty] | 2019 | July | 30 | 16 | 4118 | 28500 | 14.45%
[29 empty] | 2019 | July | 30 | 17 | 7344.5 | 28500 | 25.77%
[29 empty] | 2019 | July | 30 | 18 | 2645 | 28500 | 9.281%
[29 empty] | 2019 | July | 30 | 19 | 462 | 28500 | 1.621%
[29 empty] | 2019 | July | 30 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 30 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 30 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 30 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 31 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 31 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 31 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 31 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 31 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 31 | 5 | 182.5 | 28500 | 0.6404%
[29 empty] | 2019 | July | 31 | 6 | 1313.5 | 28500 | 4.609%
[29 empty] | 2019 | July | 31 | 7 | 2424 | 28500 | 8.505%
[29 empty] | 2019 | July | 31 | 8 | 15753.5 | 28500 | 55.28%
[29 empty] | 2019 | July | 31 | 9 | 26536 | 28500 | 93.11%
[29 empty] | 2019 | July | 31 | 10 | 18587 | 28500 | 65.22%
[29 empty] | 2019 | July | 31 | 11 | 12960 | 28500 | 45.47%
[29 empty] | 2019 | July | 31 | 12 | 15873.5 | 28500 | 55.7%
[29 empty] | 2019 | July | 31 | 13 | 24217.5 | 28500 | 84.97%
[29 empty] | 2019 | July | 31 | 14 | 24748 | 28500 | 86.84%
[29 empty] | 2019 | July | 31 | 15 | 26076.5 | 28500 | 91.5%
[29 empty] | 2019 | July | 31 | 16 | 17205 | 28500 | 60.37%
[29 empty] | 2019 | July | 31 | 17 | 8418 | 28500 | 29.54%
[29 empty] | 2019 | July | 31 | 18 | 2694 | 28500 | 9.453%
[29 empty] | 2019 | July | 31 | 19 | 483 | 28500 | 1.695%
[29 empty] | 2019 | July | 31 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 31 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 31 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | July | 31 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 1 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 1 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 1 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 1 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 1 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 1 | 5 | 727.5 | 28500 | 2.553%
[29 empty] | 2019 | August | 1 | 6 | 3044 | 28500 | 10.68%
[29 empty] | 2019 | August | 1 | 7 | 8722.5 | 28500 | 30.61%
[29 empty] | 2019 | August | 1 | 8 | 12621.5 | 28500 | 44.29%
[29 empty] | 2019 | August | 1 | 9 | 15150 | 28500 | 53.16%
[29 empty] | 2019 | August | 1 | 10 | 8707 | 28500 | 30.55%
[29 empty] | 2019 | August | 1 | 11 | 7602 | 28500 | 26.67%
[29 empty] | 2019 | August | 1 | 12 | 28787.5 | 28500 | 101%
[29 empty] | 2019 | August | 1 | 13 | 23668.5 | 28500 | 83.05%
[29 empty] | 2019 | August | 1 | 14 | 27862 | 28500 | 97.76%
[29 empty] | 2019 | August | 1 | 15 | 20494 | 28500 | 71.91%
[29 empty] | 2019 | August | 1 | 16 | 17931.5 | 28500 | 62.92%
[29 empty] | 2019 | August | 1 | 17 | 7308.5 | 28500 | 25.64%
[29 empty] | 2019 | August | 1 | 18 | 2707 | 28500 | 9.498%
[29 empty] | 2019 | August | 1 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 1 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 1 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 1 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 1 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 2 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 2 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 2 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 2 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 2 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 2 | 5 | 207 | 28500 | 0.7263%
[29 empty] | 2019 | August | 2 | 6 | 2855.5 | 28500 | 10.02%
[29 empty] | 2019 | August | 2 | 7 | 4923 | 28500 | 17.27%
[29 empty] | 2019 | August | 2 | 8 | 6419 | 28500 | 22.52%
[29 empty] | 2019 | August | 2 | 9 | 15841.5 | 28500 | 55.58%
[29 empty] | 2019 | August | 2 | 10 | 16873 | 28500 | 59.2%
[29 empty] | 2019 | August | 2 | 11 | 28201.5 | 28500 | 98.95%
[29 empty] | 2019 | August | 2 | 12 | 35439.5 | 28500 | 124.3%
[29 empty] | 2019 | August | 2 | 13 | 8820 | 28500 | 30.95%
[29 empty] | 2019 | August | 2 | 14 | 28737.5 | 28500 | 100.8%
[29 empty] | 2019 | August | 2 | 15 | 26273.5 | 28500 | 92.19%
[29 empty] | 2019 | August | 2 | 16 | 1544.5 | 28500 | 5.419%
[29 empty] | 2019 | August | 2 | 17 | 8603 | 28500 | 30.19%
[29 empty] | 2019 | August | 2 | 18 | 2672.5 | 28500 | 9.377%
[29 empty] | 2019 | August | 2 | 19 | 373 | 28500 | 1.309%
[29 empty] | 2019 | August | 2 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 2 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 2 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 2 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 3 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 3 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 3 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 3 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 3 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 3 | 5 | 472.5 | 28500 | 1.658%
[29 empty] | 2019 | August | 3 | 6 | 3209.5 | 28500 | 11.26%
[29 empty] | 2019 | August | 3 | 7 | 10214.5 | 28500 | 35.84%
[29 empty] | 2019 | August | 3 | 8 | 13772.5 | 28500 | 48.32%
[29 empty] | 2019 | August | 3 | 9 | 20162 | 28500 | 70.74%
[29 empty] | 2019 | August | 3 | 10 | 24185 | 28500 | 84.86%
[29 empty] | 2019 | August | 3 | 11 | 24235 | 28500 | 85.04%
[29 empty] | 2019 | August | 3 | 12 | 20662.5 | 28500 | 72.5%
[29 empty] | 2019 | August | 3 | 13 | 16322 | 28500 | 57.27%
[29 empty] | 2019 | August | 3 | 14 | 11008.5 | 28500 | 38.63%
[29 empty] | 2019 | August | 3 | 15 | 9223.5 | 28500 | 32.36%
[29 empty] | 2019 | August | 3 | 16 | 4201 | 28500 | 14.74%
[29 empty] | 2019 | August | 3 | 17 | 3032.5 | 28500 | 10.64%
[29 empty] | 2019 | August | 3 | 18 | 1272 | 28500 | 4.463%
[29 empty] | 2019 | August | 3 | 19 | 2 | 28500 | 0.007018%
[29 empty] | 2019 | August | 3 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 3 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 3 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 3 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 4 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 4 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 4 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 4 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 4 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 4 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 4 | 6 | 3213 | 28500 | 11.27%
[29 empty] | 2019 | August | 4 | 7 | 7074.5 | 28500 | 24.82%
[29 empty] | 2019 | August | 4 | 8 | 9556.5 | 28500 | 33.53%
[29 empty] | 2019 | August | 4 | 9 | 14511.5 | 28500 | 50.92%
[29 empty] | 2019 | August | 4 | 10 | 24900 | 28500 | 87.37%
[29 empty] | 2019 | August | 4 | 11 | 22370 | 28500 | 78.49%
[29 empty] | 2019 | August | 4 | 12 | 21499 | 28500 | 75.44%
[29 empty] | 2019 | August | 4 | 13 | 24299.5 | 28500 | 85.26%
[29 empty] | 2019 | August | 4 | 14 | 27840.5 | 28500 | 97.69%
[29 empty] | 2019 | August | 4 | 15 | 7476.5 | 28500 | 26.23%
[29 empty] | 2019 | August | 4 | 16 | 1572 | 28500 | 5.516%
[29 empty] | 2019 | August | 4 | 17 | 1236.5 | 28500 | 4.339%
[29 empty] | 2019 | August | 4 | 18 | 179.5 | 28500 | 0.6298%
[29 empty] | 2019 | August | 4 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 4 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 4 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 4 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 4 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 5 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 5 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 5 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 5 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 5 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 5 | 5 | 3.5 | 28500 | 0.01228%
[29 empty] | 2019 | August | 5 | 6 | 1697.5 | 28500 | 5.956%
[29 empty] | 2019 | August | 5 | 7 | 9196.5 | 28500 | 32.27%
[29 empty] | 2019 | August | 5 | 8 | 9555 | 28500 | 33.53%
[29 empty] | 2019 | August | 5 | 9 | 4943.5 | 28500 | 17.35%
[29 empty] | 2019 | August | 5 | 10 | 4437 | 28500 | 15.57%
[29 empty] | 2019 | August | 5 | 11 | 23211.5 | 28500 | 81.44%
[29 empty] | 2019 | August | 5 | 12 | 31678.5 | 28500 | 111.2%
[29 empty] | 2019 | August | 5 | 13 | 30076.5 | 28500 | 105.5%
[29 empty] | 2019 | August | 5 | 14 | 20642.5 | 28500 | 72.43%
[29 empty] | 2019 | August | 5 | 15 | 20757 | 28500 | 72.83%
[29 empty] | 2019 | August | 5 | 16 | 13990.5 | 28500 | 49.09%
[29 empty] | 2019 | August | 5 | 17 | 9180 | 28500 | 32.21%
[29 empty] | 2019 | August | 5 | 18 | 1988 | 28500 | 6.975%
[29 empty] | 2019 | August | 5 | 19 | 248 | 28500 | 0.8702%
[29 empty] | 2019 | August | 5 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 5 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 5 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 5 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 6 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 6 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 6 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 6 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 6 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 6 | 5 | 525.5 | 28500 | 1.844%
[29 empty] | 2019 | August | 6 | 6 | 2779 | 28500 | 9.751%
[29 empty] | 2019 | August | 6 | 7 | 10948.5 | 28500 | 38.42%
[29 empty] | 2019 | August | 6 | 8 | 19303 | 28500 | 67.73%
[29 empty] | 2019 | August | 6 | 9 | 27467 | 28500 | 96.38%
[29 empty] | 2019 | August | 6 | 10 | 25917.5 | 28500 | 90.94%
[29 empty] | 2019 | August | 6 | 11 | 26656.5 | 28500 | 93.53%
[29 empty] | 2019 | August | 6 | 12 | 18427 | 28500 | 64.66%
[29 empty] | 2019 | August | 6 | 13 | 20981 | 28500 | 73.62%
[29 empty] | 2019 | August | 6 | 14 | 29299 | 28500 | 102.8%
[29 empty] | 2019 | August | 6 | 15 | 15350 | 28500 | 53.86%
[29 empty] | 2019 | August | 6 | 16 | 15580 | 28500 | 54.67%
[29 empty] | 2019 | August | 6 | 17 | 8774.5 | 28500 | 30.79%
[29 empty] | 2019 | August | 6 | 18 | 2239 | 28500 | 7.856%
[29 empty] | 2019 | August | 6 | 19 | 202 | 28500 | 0.7088%
[29 empty] | 2019 | August | 6 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 6 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 6 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 6 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 7 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 7 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 7 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 7 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 7 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 7 | 5 | 497.5 | 28500 | 1.746%
[29 empty] | 2019 | August | 7 | 6 | 3001 | 28500 | 10.53%
[29 empty] | 2019 | August | 7 | 7 | 10629 | 28500 | 37.29%
[29 empty] | 2019 | August | 7 | 8 | 19799.5 | 28500 | 69.47%
[29 empty] | 2019 | August | 7 | 9 | 15915.5 | 28500 | 55.84%
[29 empty] | 2019 | August | 7 | 10 | 28896 | 28500 | 101.4%
[29 empty] | 2019 | August | 7 | 11 | 20123 | 28500 | 70.61%
[29 empty] | 2019 | August | 7 | 12 | 32769 | 28500 | 115%
[29 empty] | 2019 | August | 7 | 13 | 3612.5 | 28500 | 12.68%
[29 empty] | 2019 | August | 7 | 14 | 29655.5 | 28500 | 104.1%
[29 empty] | 2019 | August | 7 | 15 | 14088 | 28500 | 49.43%
[29 empty] | 2019 | August | 7 | 16 | 14211 | 28500 | 49.86%
[29 empty] | 2019 | August | 7 | 17 | 6900 | 28500 | 24.21%
[29 empty] | 2019 | August | 7 | 18 | 1483 | 28500 | 5.204%
[29 empty] | 2019 | August | 7 | 19 | 133 | 28500 | 0.4667%
[29 empty] | 2019 | August | 7 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 7 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 7 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 7 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 8 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 8 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 8 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 8 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 8 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 8 | 5 | 309.5 | 28500 | 1.086%
[29 empty] | 2019 | August | 8 | 6 | 3022 | 28500 | 10.6%
[29 empty] | 2019 | August | 8 | 7 | 8405.5 | 28500 | 29.49%
[29 empty] | 2019 | August | 8 | 8 | 18788.5 | 28500 | 65.92%
[29 empty] | 2019 | August | 8 | 9 | 28350 | 28500 | 99.47%
[29 empty] | 2019 | August | 8 | 10 | 25553.5 | 28500 | 89.66%
[29 empty] | 2019 | August | 8 | 11 | 26068 | 28500 | 91.47%
[29 empty] | 2019 | August | 8 | 12 | 13322 | 28500 | 46.74%
[29 empty] | 2019 | August | 8 | 13 | 33455 | 28500 | 117.4%
[29 empty] | 2019 | August | 8 | 14 | 26790 | 28500 | 94%
[29 empty] | 2019 | August | 8 | 15 | 10081.5 | 28500 | 35.37%
[29 empty] | 2019 | August | 8 | 16 | 9515.5 | 28500 | 33.39%
[29 empty] | 2019 | August | 8 | 17 | 7572 | 28500 | 26.57%
[29 empty] | 2019 | August | 8 | 18 | 1907.5 | 28500 | 6.693%
[29 empty] | 2019 | August | 8 | 19 | 90 | 28500 | 0.3158%
[29 empty] | 2019 | August | 8 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 8 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 8 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 8 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 9 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 9 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 9 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 9 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 9 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 9 | 5 | 202.5 | 28500 | 0.7105%
[29 empty] | 2019 | August | 9 | 6 | 1362 | 28500 | 4.779%
[29 empty] | 2019 | August | 9 | 7 | 7512.5 | 28500 | 26.36%
[29 empty] | 2019 | August | 9 | 8 | 1525.5 | 28500 | 5.353%
[29 empty] | 2019 | August | 9 | 9 | 12852.5 | 28500 | 45.1%
[29 empty] | 2019 | August | 9 | 10 | 21977.5 | 28500 | 77.11%
[29 empty] | 2019 | August | 9 | 11 | 29800 | 28500 | 104.6%
[29 empty] | 2019 | August | 9 | 12 | 31506.5 | 28500 | 110.5%
[29 empty] | 2019 | August | 9 | 13 | 14299 | 28500 | 50.17%
[29 empty] | 2019 | August | 9 | 14 | 22202 | 28500 | 77.9%
[29 empty] | 2019 | August | 9 | 15 | 11251 | 28500 | 39.48%
[29 empty] | 2019 | August | 9 | 16 | 12029.5 | 28500 | 42.21%
[29 empty] | 2019 | August | 9 | 17 | 6746.5 | 28500 | 23.67%
[29 empty] | 2019 | August | 9 | 18 | 2091 | 28500 | 7.337%
[29 empty] | 2019 | August | 9 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 9 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 9 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 9 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 9 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 10 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 10 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 10 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 10 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 10 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 10 | 5 | 278.5 | 28500 | 0.9772%
[29 empty] | 2019 | August | 10 | 6 | 2540.5 | 28500 | 8.914%
[29 empty] | 2019 | August | 10 | 7 | 3647.5 | 28500 | 12.8%
[29 empty] | 2019 | August | 10 | 8 | 11449 | 28500 | 40.17%
[29 empty] | 2019 | August | 10 | 9 | 19292.5 | 28500 | 67.69%
[29 empty] | 2019 | August | 10 | 10 | 5302.5 | 28500 | 18.61%
[29 empty] | 2019 | August | 10 | 11 | 36790.5 | 28500 | 129.1%
[29 empty] | 2019 | August | 10 | 12 | 27525 | 28500 | 96.58%
[29 empty] | 2019 | August | 10 | 13 | 35384 | 28500 | 124.2%
[29 empty] | 2019 | August | 10 | 14 | 22000.5 | 28500 | 77.19%
[29 empty] | 2019 | August | 10 | 15 | 19570.5 | 28500 | 68.67%
[29 empty] | 2019 | August | 10 | 16 | 18064.5 | 28500 | 63.38%
[29 empty] | 2019 | August | 10 | 17 | 8829.5 | 28500 | 30.98%
[29 empty] | 2019 | August | 10 | 18 | 1780.5 | 28500 | 6.247%
[29 empty] | 2019 | August | 10 | 19 | 53.5 | 28500 | 0.1877%
[29 empty] | 2019 | August | 10 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 10 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 10 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 10 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 11 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 11 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 11 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 11 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 11 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 11 | 5 | 307.5 | 28500 | 1.079%
[29 empty] | 2019 | August | 11 | 6 | 2228.5 | 28500 | 7.819%
[29 empty] | 2019 | August | 11 | 7 | 10796 | 28500 | 37.88%
[29 empty] | 2019 | August | 11 | 8 | 14456.5 | 28500 | 50.72%
[29 empty] | 2019 | August | 11 | 9 | 23828.5 | 28500 | 83.61%
[29 empty] | 2019 | August | 11 | 10 | 23496.5 | 28500 | 82.44%
[29 empty] | 2019 | August | 11 | 11 | 28067 | 28500 | 98.48%
[29 empty] | 2019 | August | 11 | 12 | 32888 | 28500 | 115.4%
[29 empty] | 2019 | August | 11 | 13 | 24963.5 | 28500 | 87.59%
[29 empty] | 2019 | August | 11 | 14 | 24897 | 28500 | 87.36%
[29 empty] | 2019 | August | 11 | 15 | 15075.5 | 28500 | 52.9%
[29 empty] | 2019 | August | 11 | 16 | 7079.5 | 28500 | 24.84%
[29 empty] | 2019 | August | 11 | 17 | 2461.5 | 28500 | 8.637%
[29 empty] | 2019 | August | 11 | 18 | 1492.5 | 28500 | 5.237%
[29 empty] | 2019 | August | 11 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 11 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 11 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 11 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 11 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 12 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 12 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 12 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 12 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 12 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 12 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 12 | 6 | 2476.5 | 28500 | 8.689%
[29 empty] | 2019 | August | 12 | 7 | 5496 | 28500 | 19.28%
[29 empty] | 2019 | August | 12 | 8 | 8114.5 | 28500 | 28.47%
[29 empty] | 2019 | August | 12 | 9 | 15027.5 | 28500 | 52.73%
[29 empty] | 2019 | August | 12 | 10 | 2297.5 | 28500 | 8.061%
[29 empty] | 2019 | August | 12 | 11 | 7898.5 | 28500 | 27.71%
[29 empty] | 2019 | August | 12 | 12 | 12667.5 | 28500 | 44.45%
[29 empty] | 2019 | August | 12 | 13 | 4691.5 | 28500 | 16.46%
[29 empty] | 2019 | August | 12 | 14 | 2075.5 | 28500 | 7.282%
[29 empty] | 2019 | August | 12 | 15 | 23352 | 28500 | 81.94%
[29 empty] | 2019 | August | 12 | 16 | 3530.5 | 28500 | 12.39%
[29 empty] | 2019 | August | 12 | 17 | 2452.5 | 28500 | 8.605%
[29 empty] | 2019 | August | 12 | 18 | 2082.5 | 28500 | 7.307%
[29 empty] | 2019 | August | 12 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 12 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 12 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 12 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 12 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 13 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 13 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 13 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 13 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 13 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 13 | 5 | 236.5 | 28500 | 0.8298%
[29 empty] | 2019 | August | 13 | 6 | 992.5 | 28500 | 3.482%
[29 empty] | 2019 | August | 13 | 7 | 7787.5 | 28500 | 27.32%
[29 empty] | 2019 | August | 13 | 8 | 17338 | 28500 | 60.84%
[29 empty] | 2019 | August | 13 | 9 | 30000 | 28500 | 105.3%
[29 empty] | 2019 | August | 13 | 10 | 34601 | 28500 | 121.4%
[29 empty] | 2019 | August | 13 | 11 | 32540 | 28500 | 114.2%
[29 empty] | 2019 | August | 13 | 12 | 23220 | 28500 | 81.47%
[29 empty] | 2019 | August | 13 | 13 | 37522.5 | 28500 | 131.7%
[29 empty] | 2019 | August | 13 | 14 | 33762 | 28500 | 118.5%
[29 empty] | 2019 | August | 13 | 15 | 26171.5 | 28500 | 91.83%
[29 empty] | 2019 | August | 13 | 16 | 12496 | 28500 | 43.85%
[29 empty] | 2019 | August | 13 | 17 | 8208.5 | 28500 | 28.8%
[29 empty] | 2019 | August | 13 | 18 | 1192 | 28500 | 4.182%
[29 empty] | 2019 | August | 13 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 13 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 13 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 13 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 13 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 14 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 14 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 14 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 14 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 14 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 14 | 5 | 210 | 28500 | 0.7368%
[29 empty] | 2019 | August | 14 | 6 | 1541 | 28500 | 5.407%
[29 empty] | 2019 | August | 14 | 7 | 3151 | 28500 | 11.06%
[29 empty] | 2019 | August | 14 | 8 | 1177.5 | 28500 | 4.132%
[29 empty] | 2019 | August | 14 | 9 | 3789 | 28500 | 13.29%
[29 empty] | 2019 | August | 14 | 10 | 3371 | 28500 | 11.83%
[29 empty] | 2019 | August | 14 | 11 | 3175 | 28500 | 11.14%
[29 empty] | 2019 | August | 14 | 12 | 2054 | 28500 | 7.207%
[29 empty] | 2019 | August | 14 | 13 | 3773.5 | 28500 | 13.24%
[29 empty] | 2019 | August | 14 | 14 | 1909.5 | 28500 | 6.7%
[29 empty] | 2019 | August | 14 | 15 | 4881 | 28500 | 17.13%
[29 empty] | 2019 | August | 14 | 16 | 4881.5 | 28500 | 17.13%
[29 empty] | 2019 | August | 14 | 17 | 4675 | 28500 | 16.4%
[29 empty] | 2019 | August | 14 | 18 | 1169 | 28500 | 4.102%
[29 empty] | 2019 | August | 14 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 14 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 14 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 14 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 14 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 15 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 15 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 15 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 15 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 15 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 15 | 5 | 116 | 28500 | 0.407%
[29 empty] | 2019 | August | 15 | 6 | 2355.5 | 28500 | 8.265%
[29 empty] | 2019 | August | 15 | 7 | 2992 | 28500 | 10.5%
[29 empty] | 2019 | August | 15 | 8 | 16519 | 28500 | 57.96%
[29 empty] | 2019 | August | 15 | 9 | 19950.5 | 28500 | 70%
[29 empty] | 2019 | August | 15 | 10 | 17063.5 | 28500 | 59.87%
[29 empty] | 2019 | August | 15 | 11 | 16232.5 | 28500 | 56.96%
[29 empty] | 2019 | August | 15 | 12 | 25743 | 28500 | 90.33%
[29 empty] | 2019 | August | 15 | 13 | 38256 | 28500 | 134.2%
[29 empty] | 2019 | August | 15 | 14 | 32171 | 28500 | 112.9%
[29 empty] | 2019 | August | 15 | 15 | 24682 | 28500 | 86.6%
[29 empty] | 2019 | August | 15 | 16 | 16972.5 | 28500 | 59.55%
[29 empty] | 2019 | August | 15 | 17 | 3105.5 | 28500 | 10.9%
[29 empty] | 2019 | August | 15 | 18 | 1088 | 28500 | 3.818%
[29 empty] | 2019 | August | 15 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 15 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 15 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 15 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 15 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 16 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 16 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 16 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 16 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 16 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 16 | 5 | 117.5 | 28500 | 0.4123%
[29 empty] | 2019 | August | 16 | 6 | 2529.5 | 28500 | 8.875%
[29 empty] | 2019 | August | 16 | 7 | 1280 | 28500 | 4.491%
[29 empty] | 2019 | August | 16 | 8 | 5988 | 28500 | 21.01%
[29 empty] | 2019 | August | 16 | 9 | 2007 | 28500 | 7.042%
[29 empty] | 2019 | August | 16 | 10 | 4511 | 28500 | 15.83%
[29 empty] | 2019 | August | 16 | 11 | 10218.5 | 28500 | 35.85%
[29 empty] | 2019 | August | 16 | 12 | 4478 | 28500 | 15.71%
[29 empty] | 2019 | August | 16 | 13 | 8878 | 28500 | 31.15%
[29 empty] | 2019 | August | 16 | 14 | 3417 | 28500 | 11.99%
[29 empty] | 2019 | August | 16 | 15 | 2452.5 | 28500 | 8.605%
[29 empty] | 2019 | August | 16 | 16 | 2056 | 28500 | 7.214%
[29 empty] | 2019 | August | 16 | 17 | 678 | 28500 | 2.379%
[29 empty] | 2019 | August | 16 | 18 | 113 | 28500 | 0.3965%
[29 empty] | 2019 | August | 16 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 16 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 16 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 16 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 16 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 17 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 17 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 17 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 17 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 17 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 17 | 5 | 36 | 28500 | 0.1263%
[29 empty] | 2019 | August | 17 | 6 | 2400.5 | 28500 | 8.423%
[29 empty] | 2019 | August | 17 | 7 | 10290.5 | 28500 | 36.11%
[29 empty] | 2019 | August | 17 | 8 | 8299 | 28500 | 29.12%
[29 empty] | 2019 | August | 17 | 9 | 7734.5 | 28500 | 27.14%
[29 empty] | 2019 | August | 17 | 10 | 11926.5 | 28500 | 41.85%
[29 empty] | 2019 | August | 17 | 11 | 26514 | 28500 | 93.03%
[29 empty] | 2019 | August | 17 | 12 | 20249 | 28500 | 71.05%
[29 empty] | 2019 | August | 17 | 13 | 15540.5 | 28500 | 54.53%
[29 empty] | 2019 | August | 17 | 14 | 23292 | 28500 | 81.73%
[29 empty] | 2019 | August | 17 | 15 | 25246.5 | 28500 | 88.58%
[29 empty] | 2019 | August | 17 | 16 | 7679 | 28500 | 26.94%
[29 empty] | 2019 | August | 17 | 17 | 1425.5 | 28500 | 5.002%
[29 empty] | 2019 | August | 17 | 18 | 699.5 | 28500 | 2.454%
[29 empty] | 2019 | August | 17 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 17 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 17 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 17 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 17 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 18 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 18 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 18 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 18 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 18 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 18 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 18 | 6 | 2063.5 | 28500 | 7.24%
[29 empty] | 2019 | August | 18 | 7 | 6632.5 | 28500 | 23.27%
[29 empty] | 2019 | August | 18 | 8 | 15877 | 28500 | 55.71%
[29 empty] | 2019 | August | 18 | 9 | 2501 | 28500 | 8.775%
[29 empty] | 2019 | August | 18 | 10 | 4621 | 28500 | 16.21%
[29 empty] | 2019 | August | 18 | 11 | 20364.5 | 28500 | 71.45%
[29 empty] | 2019 | August | 18 | 12 | 15290.5 | 28500 | 53.65%
[29 empty] | 2019 | August | 18 | 13 | 36273 | 28500 | 127.3%
[29 empty] | 2019 | August | 18 | 14 | 24959.5 | 28500 | 87.58%
[29 empty] | 2019 | August | 18 | 15 | 4315 | 28500 | 15.14%
[29 empty] | 2019 | August | 18 | 16 | 18718 | 28500 | 65.68%
[29 empty] | 2019 | August | 18 | 17 | 6098.5 | 28500 | 21.4%
[29 empty] | 2019 | August | 18 | 18 | 1152 | 28500 | 4.042%
[29 empty] | 2019 | August | 18 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 18 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 18 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 18 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 18 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 19 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 19 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 19 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 19 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 19 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 19 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 19 | 6 | 2452 | 28500 | 8.604%
[29 empty] | 2019 | August | 19 | 7 | 8164.5 | 28500 | 28.65%
[29 empty] | 2019 | August | 19 | 8 | 20710.5 | 28500 | 72.67%
[29 empty] | 2019 | August | 19 | 9 | 24562 | 28500 | 86.18%
[29 empty] | 2019 | August | 19 | 10 | 30647 | 28500 | 107.5%
[29 empty] | 2019 | August | 19 | 11 | 21692.5 | 28500 | 76.11%
[29 empty] | 2019 | August | 19 | 12 | 19158 | 28500 | 67.22%
[29 empty] | 2019 | August | 19 | 13 | 1884.5 | 28500 | 6.612%
[29 empty] | 2019 | August | 19 | 14 | 17394.5 | 28500 | 61.03%
[29 empty] | 2019 | August | 19 | 15 | 22450.5 | 28500 | 78.77%
[29 empty] | 2019 | August | 19 | 16 | 5380 | 28500 | 18.88%
[29 empty] | 2019 | August | 19 | 17 | 8187.5 | 28500 | 28.73%
[29 empty] | 2019 | August | 19 | 18 | 1184 | 28500 | 4.154%
[29 empty] | 2019 | August | 19 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 19 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 19 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 19 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 19 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 20 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 20 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 20 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 20 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 20 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 20 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 20 | 6 | 2351.5 | 28500 | 8.251%
[29 empty] | 2019 | August | 20 | 7 | 11058 | 28500 | 38.8%
[29 empty] | 2019 | August | 20 | 8 | 21486.5 | 28500 | 75.39%
[29 empty] | 2019 | August | 20 | 9 | 29373.5 | 28500 | 103.1%
[29 empty] | 2019 | August | 20 | 10 | 29584 | 28500 | 103.8%
[29 empty] | 2019 | August | 20 | 11 | 33738.5 | 28500 | 118.4%
[29 empty] | 2019 | August | 20 | 12 | 32821 | 28500 | 115.2%
[29 empty] | 2019 | August | 20 | 13 | 33351.5 | 28500 | 117%
[29 empty] | 2019 | August | 20 | 14 | 28526.5 | 28500 | 100.1%
[29 empty] | 2019 | August | 20 | 15 | 26574 | 28500 | 93.24%
[29 empty] | 2019 | August | 20 | 16 | 17597.5 | 28500 | 61.75%
[29 empty] | 2019 | August | 20 | 17 | 8157.5 | 28500 | 28.62%
[29 empty] | 2019 | August | 20 | 18 | 1284 | 28500 | 4.505%
[29 empty] | 2019 | August | 20 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 20 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 20 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 20 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 20 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 21 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 21 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 21 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 21 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 21 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 21 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 21 | 6 | 2229.5 | 28500 | 7.823%
[29 empty] | 2019 | August | 21 | 7 | 9563.5 | 28500 | 33.56%
[29 empty] | 2019 | August | 21 | 8 | 15201 | 28500 | 53.34%
[29 empty] | 2019 | August | 21 | 9 | 23658.5 | 28500 | 83.01%
[29 empty] | 2019 | August | 21 | 10 | 30812.5 | 28500 | 108.1%
[29 empty] | 2019 | August | 21 | 11 | 33066 | 28500 | 116%
[29 empty] | 2019 | August | 21 | 12 | 29735 | 28500 | 104.3%
[29 empty] | 2019 | August | 21 | 13 | 21353.5 | 28500 | 74.92%
[29 empty] | 2019 | August | 21 | 14 | 26178 | 28500 | 91.85%
[29 empty] | 2019 | August | 21 | 15 | 21312 | 28500 | 74.78%
[29 empty] | 2019 | August | 21 | 16 | 17510.5 | 28500 | 61.44%
[29 empty] | 2019 | August | 21 | 17 | 8022.5 | 28500 | 28.15%
[29 empty] | 2019 | August | 21 | 18 | 882.5 | 28500 | 3.096%
[29 empty] | 2019 | August | 21 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 21 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 21 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 21 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 21 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 22 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 22 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 22 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 22 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 22 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 22 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 22 | 6 | 1967 | 28500 | 6.902%
[29 empty] | 2019 | August | 22 | 7 | 10707 | 28500 | 37.57%
[29 empty] | 2019 | August | 22 | 8 | 20659.5 | 28500 | 72.49%
[29 empty] | 2019 | August | 22 | 9 | 28962 | 28500 | 101.6%
[29 empty] | 2019 | August | 22 | 10 | 34930.5 | 28500 | 122.6%
[29 empty] | 2019 | August | 22 | 11 | 37605.5 | 28500 | 131.9%
[29 empty] | 2019 | August | 22 | 12 | 37894.5 | 28500 | 133%
[29 empty] | 2019 | August | 22 | 13 | 38812 | 28500 | 136.2%
[29 empty] | 2019 | August | 22 | 14 | 32253 | 28500 | 113.2%
[29 empty] | 2019 | August | 22 | 15 | 27160.5 | 28500 | 95.3%
[29 empty] | 2019 | August | 22 | 16 | 18603 | 28500 | 65.27%
[29 empty] | 2019 | August | 22 | 17 | 7737 | 28500 | 27.15%
[29 empty] | 2019 | August | 22 | 18 | 857.5 | 28500 | 3.009%
[29 empty] | 2019 | August | 22 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 22 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 22 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 22 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 22 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 23 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 23 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 23 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 23 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 23 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 23 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 23 | 6 | 2108.5 | 28500 | 7.398%
[29 empty] | 2019 | August | 23 | 7 | 8002.5 | 28500 | 28.08%
[29 empty] | 2019 | August | 23 | 8 | 17410 | 28500 | 61.09%
[29 empty] | 2019 | August | 23 | 9 | 27617 | 28500 | 96.9%
[29 empty] | 2019 | August | 23 | 10 | 29381 | 28500 | 103.1%
[29 empty] | 2019 | August | 23 | 11 | 36294 | 28500 | 127.3%
[29 empty] | 2019 | August | 23 | 12 | 36746 | 28500 | 128.9%
[29 empty] | 2019 | August | 23 | 13 | 35994 | 28500 | 126.3%
[29 empty] | 2019 | August | 23 | 14 | 32304.5 | 28500 | 113.3%
[29 empty] | 2019 | August | 23 | 15 | 24812 | 28500 | 87.06%
[29 empty] | 2019 | August | 23 | 16 | 18034 | 28500 | 63.28%
[29 empty] | 2019 | August | 23 | 17 | 7385.5 | 28500 | 25.91%
[29 empty] | 2019 | August | 23 | 18 | 869 | 28500 | 3.049%
[29 empty] | 2019 | August | 23 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 23 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 23 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 23 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 23 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 24 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 24 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 24 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 24 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 24 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 24 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 24 | 6 | 2183.5 | 28500 | 7.661%
[29 empty] | 2019 | August | 24 | 7 | 8589 | 28500 | 30.14%
[29 empty] | 2019 | August | 24 | 8 | 17571.5 | 28500 | 61.65%
[29 empty] | 2019 | August | 24 | 9 | 23303.5 | 28500 | 81.77%
[29 empty] | 2019 | August | 24 | 10 | 31760.5 | 28500 | 111.4%
[29 empty] | 2019 | August | 24 | 11 | 37034 | 28500 | 129.9%
[29 empty] | 2019 | August | 24 | 12 | 37354.5 | 28500 | 131.1%
[29 empty] | 2019 | August | 24 | 13 | 37345.5 | 28500 | 131%
[29 empty] | 2019 | August | 24 | 14 | 29115 | 28500 | 102.2%
[29 empty] | 2019 | August | 24 | 15 | 19591.5 | 28500 | 68.74%
[29 empty] | 2019 | August | 24 | 16 | 11349 | 28500 | 39.82%
[29 empty] | 2019 | August | 24 | 17 | 5670.5 | 28500 | 19.9%
[29 empty] | 2019 | August | 24 | 18 | 1141 | 28500 | 4.004%
[29 empty] | 2019 | August | 24 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 24 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 24 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 24 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 24 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 25 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 25 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 25 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 25 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 25 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 25 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 25 | 6 | 266 | 28500 | 0.9333%
[29 empty] | 2019 | August | 25 | 7 | 7230.5 | 28500 | 25.37%
[29 empty] | 2019 | August | 25 | 8 | 19501.5 | 28500 | 68.43%
[29 empty] | 2019 | August | 25 | 9 | 27138.5 | 28500 | 95.22%
[29 empty] | 2019 | August | 25 | 10 | 33043.5 | 28500 | 115.9%
[29 empty] | 2019 | August | 25 | 11 | 36059 | 28500 | 126.5%
[29 empty] | 2019 | August | 25 | 12 | 31524.5 | 28500 | 110.6%
[29 empty] | 2019 | August | 25 | 13 | 36730 | 28500 | 128.9%
[29 empty] | 2019 | August | 25 | 14 | 31762.5 | 28500 | 111.4%
[29 empty] | 2019 | August | 25 | 15 | 26146 | 28500 | 91.74%
[29 empty] | 2019 | August | 25 | 16 | 17357 | 28500 | 60.9%
[29 empty] | 2019 | August | 25 | 17 | 6896 | 28500 | 24.2%
[29 empty] | 2019 | August | 25 | 18 | 942 | 28500 | 3.305%
[29 empty] | 2019 | August | 25 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 25 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 25 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 25 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 25 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 26 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 26 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 26 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 26 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 26 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 26 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 26 | 6 | 1847 | 28500 | 6.481%
[29 empty] | 2019 | August | 26 | 7 | 10075.5 | 28500 | 35.35%
[29 empty] | 2019 | August | 26 | 8 | 19320.5 | 28500 | 67.79%
[29 empty] | 2019 | August | 26 | 9 | 26867 | 28500 | 94.27%
[29 empty] | 2019 | August | 26 | 10 | 32621.5 | 28500 | 114.5%
[29 empty] | 2019 | August | 26 | 11 | 35547 | 28500 | 124.7%
[29 empty] | 2019 | August | 26 | 12 | 37141.5 | 28500 | 130.3%
[29 empty] | 2019 | August | 26 | 13 | 36371.5 | 28500 | 127.6%
[29 empty] | 2019 | August | 26 | 14 | 31345.5 | 28500 | 110%
[29 empty] | 2019 | August | 26 | 15 | 25441.5 | 28500 | 89.27%
[29 empty] | 2019 | August | 26 | 16 | 16441 | 28500 | 57.69%
[29 empty] | 2019 | August | 26 | 17 | 6801.5 | 28500 | 23.86%
[29 empty] | 2019 | August | 26 | 18 | 853.5 | 28500 | 2.995%
[29 empty] | 2019 | August | 26 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 26 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 26 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 26 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 26 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 27 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 27 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 27 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 27 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 27 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 27 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 27 | 6 | 1887 | 28500 | 6.621%
[29 empty] | 2019 | August | 27 | 7 | 9632 | 28500 | 33.8%
[29 empty] | 2019 | August | 27 | 8 | 18429 | 28500 | 64.66%
[29 empty] | 2019 | August | 27 | 9 | 26021.5 | 28500 | 91.3%
[29 empty] | 2019 | August | 27 | 10 | 31417 | 28500 | 110.2%
[29 empty] | 2019 | August | 27 | 11 | 34483.5 | 28500 | 121%
[29 empty] | 2019 | August | 27 | 12 | 35952.5 | 28500 | 126.1%
[29 empty] | 2019 | August | 27 | 13 | 34751 | 28500 | 121.9%
[29 empty] | 2019 | August | 27 | 14 | 29663 | 28500 | 104.1%
[29 empty] | 2019 | August | 27 | 15 | 23791 | 28500 | 83.48%
[29 empty] | 2019 | August | 27 | 16 | 15729 | 28500 | 55.19%
[29 empty] | 2019 | August | 27 | 17 | 6486 | 28500 | 22.76%
[29 empty] | 2019 | August | 27 | 18 | 768 | 28500 | 2.695%
[29 empty] | 2019 | August | 27 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 27 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 27 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 27 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 27 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 28 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 28 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 28 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 28 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 28 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 28 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 28 | 6 | 68 | 28500 | 0.2386%
[29 empty] | 2019 | August | 28 | 7 | 4143.5 | 28500 | 14.54%
[29 empty] | 2019 | August | 28 | 8 | 2381 | 28500 | 8.354%
[29 empty] | 2019 | August | 28 | 9 | 9179 | 28500 | 32.21%
[29 empty] | 2019 | August | 28 | 10 | 16840 | 28500 | 59.09%
[29 empty] | 2019 | August | 28 | 11 | 37662 | 28500 | 132.1%
[29 empty] | 2019 | August | 28 | 12 | 38402.5 | 28500 | 134.7%
[29 empty] | 2019 | August | 28 | 13 | 30005 | 28500 | 105.3%
[29 empty] | 2019 | August | 28 | 14 | 28576 | 28500 | 100.3%
[29 empty] | 2019 | August | 28 | 15 | 6388 | 28500 | 22.41%
[29 empty] | 2019 | August | 28 | 16 | 7790.5 | 28500 | 27.34%
[29 empty] | 2019 | August | 28 | 17 | 3112 | 28500 | 10.92%
[29 empty] | 2019 | August | 28 | 18 | 482.5 | 28500 | 1.693%
[29 empty] | 2019 | August | 28 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 28 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 28 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 28 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 28 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 29 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 29 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 29 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 29 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 29 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 29 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 29 | 6 | 1616.5 | 28500 | 5.672%
[29 empty] | 2019 | August | 29 | 7 | 9487.5 | 28500 | 33.29%
[29 empty] | 2019 | August | 29 | 8 | 21205.5 | 28500 | 74.41%
[29 empty] | 2019 | August | 29 | 9 | 29477.5 | 28500 | 103.4%
[29 empty] | 2019 | August | 29 | 10 | 35261 | 28500 | 123.7%
[29 empty] | 2019 | August | 29 | 11 | 38139 | 28500 | 133.8%
[29 empty] | 2019 | August | 29 | 12 | 39428 | 28500 | 138.3%
[29 empty] | 2019 | August | 29 | 13 | 37703 | 28500 | 132.3%
[29 empty] | 2019 | August | 29 | 14 | 28246 | 28500 | 99.11%
[29 empty] | 2019 | August | 29 | 15 | 11670.5 | 28500 | 40.95%
[29 empty] | 2019 | August | 29 | 16 | 17000 | 28500 | 59.65%
[29 empty] | 2019 | August | 29 | 17 | 6697.5 | 28500 | 23.5%
[29 empty] | 2019 | August | 29 | 18 | 594.5 | 28500 | 2.086%
[29 empty] | 2019 | August | 29 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 29 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 29 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 29 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 29 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 30 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 30 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 30 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 30 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 30 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 30 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 30 | 6 | 1569 | 28500 | 5.505%
[29 empty] | 2019 | August | 30 | 7 | 7780.5 | 28500 | 27.3%
[29 empty] | 2019 | August | 30 | 8 | 11638 | 28500 | 40.84%
[29 empty] | 2019 | August | 30 | 9 | 19264.5 | 28500 | 67.59%
[29 empty] | 2019 | August | 30 | 10 | 27501.5 | 28500 | 96.5%
[29 empty] | 2019 | August | 30 | 11 | 32322 | 28500 | 113.4%
[29 empty] | 2019 | August | 30 | 12 | 35241.5 | 28500 | 123.7%
[29 empty] | 2019 | August | 30 | 13 | 30528 | 28500 | 107.1%
[29 empty] | 2019 | August | 30 | 14 | 31829.5 | 28500 | 111.7%
[29 empty] | 2019 | August | 30 | 15 | 26130 | 28500 | 91.68%
[29 empty] | 2019 | August | 30 | 16 | 16477.5 | 28500 | 57.82%
[29 empty] | 2019 | August | 30 | 17 | 6600.5 | 28500 | 23.16%
[29 empty] | 2019 | August | 30 | 18 | 681 | 28500 | 2.389%
[29 empty] | 2019 | August | 30 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 30 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 30 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 30 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 30 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 31 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 31 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 31 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 31 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 31 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 31 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 31 | 6 | 1626 | 28500 | 5.705%
[29 empty] | 2019 | August | 31 | 7 | 10868.5 | 28500 | 38.14%
[29 empty] | 2019 | August | 31 | 8 | 17486 | 28500 | 61.35%
[29 empty] | 2019 | August | 31 | 9 | 26942 | 28500 | 94.53%
[29 empty] | 2019 | August | 31 | 10 | 31635.5 | 28500 | 111%
[29 empty] | 2019 | August | 31 | 11 | 26006 | 28500 | 91.25%
[29 empty] | 2019 | August | 31 | 12 | 39173.5 | 28500 | 137.5%
[29 empty] | 2019 | August | 31 | 13 | 26428 | 28500 | 92.73%
[29 empty] | 2019 | August | 31 | 14 | 11571 | 28500 | 40.6%
[29 empty] | 2019 | August | 31 | 15 | 9858.5 | 28500 | 34.59%
[29 empty] | 2019 | August | 31 | 16 | 3953.5 | 28500 | 13.87%
[29 empty] | 2019 | August | 31 | 17 | 545 | 28500 | 1.912%
[29 empty] | 2019 | August | 31 | 18 | 598.5 | 28500 | 2.1%
[29 empty] | 2019 | August | 31 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 31 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 31 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 31 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | August | 31 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 1 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 1 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 1 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 1 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 1 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 1 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 1 | 6 | 217 | 28500 | 0.7614%
[29 empty] | 2019 | September | 1 | 7 | 10810.5 | 28500 | 37.93%
[29 empty] | 2019 | September | 1 | 8 | 21261 | 28500 | 74.6%
[29 empty] | 2019 | September | 1 | 9 | 29626 | 28500 | 104%
[29 empty] | 2019 | September | 1 | 10 | 31329 | 28500 | 109.9%
[29 empty] | 2019 | September | 1 | 11 | 26197 | 28500 | 91.92%
[29 empty] | 2019 | September | 1 | 12 | 2615.5 | 28500 | 9.177%
[29 empty] | 2019 | September | 1 | 13 | 26666 | 28500 | 93.56%
[29 empty] | 2019 | September | 1 | 14 | 25407 | 28500 | 89.15%
[29 empty] | 2019 | September | 1 | 15 | 14983.5 | 28500 | 52.57%
[29 empty] | 2019 | September | 1 | 16 | 15565 | 28500 | 54.61%
[29 empty] | 2019 | September | 1 | 17 | 6652.5 | 28500 | 23.34%
[29 empty] | 2019 | September | 1 | 18 | 252.5 | 28500 | 0.886%
[29 empty] | 2019 | September | 1 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 1 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 1 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 1 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 1 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 2 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 2 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 2 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 2 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 2 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 2 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 2 | 6 | 1579.5 | 28500 | 5.542%
[29 empty] | 2019 | September | 2 | 7 | 9613 | 28500 | 33.73%
[29 empty] | 2019 | September | 2 | 8 | 18147.5 | 28500 | 63.68%
[29 empty] | 2019 | September | 2 | 9 | 29291 | 28500 | 102.8%
[29 empty] | 2019 | September | 2 | 10 | 34071.5 | 28500 | 119.5%
[29 empty] | 2019 | September | 2 | 11 | 28948.5 | 28500 | 101.6%
[29 empty] | 2019 | September | 2 | 12 | 32507 | 28500 | 114.1%
[29 empty] | 2019 | September | 2 | 13 | 30909.5 | 28500 | 108.5%
[29 empty] | 2019 | September | 2 | 14 | 18829 | 28500 | 66.07%
[29 empty] | 2019 | September | 2 | 15 | 12245 | 28500 | 42.96%
[29 empty] | 2019 | September | 2 | 16 | 5194 | 28500 | 18.22%
[29 empty] | 2019 | September | 2 | 17 | 1991 | 28500 | 6.986%
[29 empty] | 2019 | September | 2 | 18 | 459 | 28500 | 1.611%
[29 empty] | 2019 | September | 2 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 2 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 2 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 2 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 2 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 3 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 3 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 3 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 3 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 3 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 3 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 3 | 6 | 1081 | 28500 | 3.793%
[29 empty] | 2019 | September | 3 | 7 | 4003.5 | 28500 | 14.05%
[29 empty] | 2019 | September | 3 | 8 | 13411.5 | 28500 | 47.06%
[29 empty] | 2019 | September | 3 | 9 | 11691 | 28500 | 41.02%
[29 empty] | 2019 | September | 3 | 10 | 14384.5 | 28500 | 50.47%
[29 empty] | 2019 | September | 3 | 11 | 17214.5 | 28500 | 60.4%
[29 empty] | 2019 | September | 3 | 12 | 16386.5 | 28500 | 57.5%
[29 empty] | 2019 | September | 3 | 13 | 15253.5 | 28500 | 53.52%
[29 empty] | 2019 | September | 3 | 14 | 20955 | 28500 | 73.53%
[29 empty] | 2019 | September | 3 | 15 | 22118.5 | 28500 | 77.61%
[29 empty] | 2019 | September | 3 | 16 | 2262 | 28500 | 7.937%
[29 empty] | 2019 | September | 3 | 17 | 2231.5 | 28500 | 7.83%
[29 empty] | 2019 | September | 3 | 18 | 111.5 | 28500 | 0.3912%
[29 empty] | 2019 | September | 3 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 3 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 3 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 3 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 3 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 4 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 4 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 4 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 4 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 4 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 4 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 4 | 6 | 29.5 | 28500 | 0.1035%
[29 empty] | 2019 | September | 4 | 7 | 2175 | 28500 | 7.632%
[29 empty] | 2019 | September | 4 | 8 | 4974.5 | 28500 | 17.45%
[29 empty] | 2019 | September | 4 | 9 | 9228 | 28500 | 32.38%
[29 empty] | 2019 | September | 4 | 10 | 21495.5 | 28500 | 75.42%
[29 empty] | 2019 | September | 4 | 11 | 19444.5 | 28500 | 68.23%
[29 empty] | 2019 | September | 4 | 12 | 35853.5 | 28500 | 125.8%
[29 empty] | 2019 | September | 4 | 13 | 36865 | 28500 | 129.4%
[29 empty] | 2019 | September | 4 | 14 | 20580.5 | 28500 | 72.21%
[29 empty] | 2019 | September | 4 | 15 | 24614.5 | 28500 | 86.37%
[29 empty] | 2019 | September | 4 | 16 | 14238.5 | 28500 | 49.96%
[29 empty] | 2019 | September | 4 | 17 | 5976 | 28500 | 20.97%
[29 empty] | 2019 | September | 4 | 18 | 354 | 28500 | 1.242%
[29 empty] | 2019 | September | 4 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 4 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 4 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 4 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 4 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 5 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 5 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 5 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 5 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 5 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 5 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 5 | 6 | 1506.5 | 28500 | 5.286%
[29 empty] | 2019 | September | 5 | 7 | 10656 | 28500 | 37.39%
[29 empty] | 2019 | September | 5 | 8 | 21539.5 | 28500 | 75.58%
[29 empty] | 2019 | September | 5 | 9 | 22208.5 | 28500 | 77.92%
[29 empty] | 2019 | September | 5 | 10 | 17005.5 | 28500 | 59.67%
[29 empty] | 2019 | September | 5 | 11 | 37920 | 28500 | 133.1%
[29 empty] | 2019 | September | 5 | 12 | 39510 | 28500 | 138.6%
[29 empty] | 2019 | September | 5 | 13 | 34844.5 | 28500 | 122.3%
[29 empty] | 2019 | September | 5 | 14 | 20657 | 28500 | 72.48%
[29 empty] | 2019 | September | 5 | 15 | 19517.5 | 28500 | 68.48%
[29 empty] | 2019 | September | 5 | 16 | 13574.5 | 28500 | 47.63%
[29 empty] | 2019 | September | 5 | 17 | 5200.5 | 28500 | 18.25%
[29 empty] | 2019 | September | 5 | 18 | 205.5 | 28500 | 0.7211%
[29 empty] | 2019 | September | 5 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 5 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 5 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 5 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 5 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 6 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 6 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 6 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 6 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 6 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 6 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 6 | 6 | 1442.5 | 28500 | 5.061%
[29 empty] | 2019 | September | 6 | 7 | 4250.5 | 28500 | 14.91%
[29 empty] | 2019 | September | 6 | 8 | 6619 | 28500 | 23.22%
[29 empty] | 2019 | September | 6 | 9 | 8624.5 | 28500 | 30.26%
[29 empty] | 2019 | September | 6 | 10 | 16209.5 | 28500 | 56.88%
[29 empty] | 2019 | September | 6 | 11 | 17417 | 28500 | 61.11%
[29 empty] | 2019 | September | 6 | 12 | 4172.5 | 28500 | 14.64%
[29 empty] | 2019 | September | 6 | 13 | 4335 | 28500 | 15.21%
[29 empty] | 2019 | September | 6 | 14 | 5961 | 28500 | 20.92%
[29 empty] | 2019 | September | 6 | 15 | 4610 | 28500 | 16.18%
[29 empty] | 2019 | September | 6 | 16 | 11145.5 | 28500 | 39.11%
[29 empty] | 2019 | September | 6 | 17 | 2197 | 28500 | 7.709%
[29 empty] | 2019 | September | 6 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 6 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 6 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 6 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 6 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 6 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 7 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 7 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 7 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 7 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 7 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 7 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 7 | 6 | 1000.5 | 28500 | 3.511%
[29 empty] | 2019 | September | 7 | 7 | 4819.5 | 28500 | 16.91%
[29 empty] | 2019 | September | 7 | 8 | 10626 | 28500 | 37.28%
[29 empty] | 2019 | September | 7 | 9 | 9868 | 28500 | 34.62%
[29 empty] | 2019 | September | 7 | 10 | 7261 | 28500 | 25.48%
[29 empty] | 2019 | September | 7 | 11 | 12160.5 | 28500 | 42.67%
[29 empty] | 2019 | September | 7 | 12 | 3878.5 | 28500 | 13.61%
[29 empty] | 2019 | September | 7 | 13 | 19701.5 | 28500 | 69.13%
[29 empty] | 2019 | September | 7 | 14 | 14374 | 28500 | 50.44%
[29 empty] | 2019 | September | 7 | 15 | 12362.5 | 28500 | 43.38%
[29 empty] | 2019 | September | 7 | 16 | 14778.5 | 28500 | 51.85%
[29 empty] | 2019 | September | 7 | 17 | 5457.5 | 28500 | 19.15%
[29 empty] | 2019 | September | 7 | 18 | 160 | 28500 | 0.5614%
[29 empty] | 2019 | September | 7 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 7 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 7 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 7 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 7 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 8 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 8 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 8 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 8 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 8 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 8 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 8 | 6 | 1394 | 28500 | 4.891%
[29 empty] | 2019 | September | 8 | 7 | 10565.5 | 28500 | 37.07%
[29 empty] | 2019 | September | 8 | 8 | 21028 | 28500 | 73.78%
[29 empty] | 2019 | September | 8 | 9 | 25211 | 28500 | 88.46%
[29 empty] | 2019 | September | 8 | 10 | 32829.5 | 28500 | 115.2%
[29 empty] | 2019 | September | 8 | 11 | 27313 | 28500 | 95.84%
[29 empty] | 2019 | September | 8 | 12 | 36402 | 28500 | 127.7%
[29 empty] | 2019 | September | 8 | 13 | 35467.5 | 28500 | 124.4%
[29 empty] | 2019 | September | 8 | 14 | 24729 | 28500 | 86.77%
[29 empty] | 2019 | September | 8 | 15 | 22485.5 | 28500 | 78.9%
[29 empty] | 2019 | September | 8 | 16 | 15290 | 28500 | 53.65%
[29 empty] | 2019 | September | 8 | 17 | 5619 | 28500 | 19.72%
[29 empty] | 2019 | September | 8 | 18 | 73.5 | 28500 | 0.2579%
[29 empty] | 2019 | September | 8 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 8 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 8 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 8 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 8 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 9 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 9 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 9 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 9 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 9 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 9 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 9 | 6 | 94 | 28500 | 0.3298%
[29 empty] | 2019 | September | 9 | 7 | 1231.5 | 28500 | 4.321%
[29 empty] | 2019 | September | 9 | 8 | 1692 | 28500 | 5.937%
[29 empty] | 2019 | September | 9 | 9 | 4722 | 28500 | 16.57%
[29 empty] | 2019 | September | 9 | 10 | 3057.5 | 28500 | 10.73%
[29 empty] | 2019 | September | 9 | 11 | 4053 | 28500 | 14.22%
[29 empty] | 2019 | September | 9 | 12 | 4051.5 | 28500 | 14.22%
[29 empty] | 2019 | September | 9 | 13 | 12599.5 | 28500 | 44.21%
[29 empty] | 2019 | September | 9 | 14 | 3396.5 | 28500 | 11.92%
[29 empty] | 2019 | September | 9 | 15 | 7164 | 28500 | 25.14%
[29 empty] | 2019 | September | 9 | 16 | 5173 | 28500 | 18.15%
[29 empty] | 2019 | September | 9 | 17 | 2388 | 28500 | 8.379%
[29 empty] | 2019 | September | 9 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 9 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 9 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 9 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 9 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 9 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 10 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 10 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 10 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 10 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 10 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 10 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 10 | 6 | 1174 | 28500 | 4.119%
[29 empty] | 2019 | September | 10 | 7 | 8225 | 28500 | 28.86%
[29 empty] | 2019 | September | 10 | 8 | 14164.5 | 28500 | 49.7%
[29 empty] | 2019 | September | 10 | 9 | 25644 | 28500 | 89.98%
[29 empty] | 2019 | September | 10 | 10 | 29483 | 28500 | 103.4%
[29 empty] | 2019 | September | 10 | 11 | 25054 | 28500 | 87.91%
[29 empty] | 2019 | September | 10 | 12 | 4387.5 | 28500 | 15.39%
[29 empty] | 2019 | September | 10 | 13 | 3630.5 | 28500 | 12.74%
[29 empty] | 2019 | September | 10 | 14 | 4424.5 | 28500 | 15.52%
[29 empty] | 2019 | September | 10 | 15 | 6547 | 28500 | 22.97%
[29 empty] | 2019 | September | 10 | 16 | 5772.5 | 28500 | 20.25%
[29 empty] | 2019 | September | 10 | 17 | 2626 | 28500 | 9.214%
[29 empty] | 2019 | September | 10 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 10 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 10 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 10 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 10 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 10 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 11 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 11 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 11 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 11 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 11 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 11 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 11 | 6 | 575 | 28500 | 2.018%
[29 empty] | 2019 | September | 11 | 7 | 2796 | 28500 | 9.811%
[29 empty] | 2019 | September | 11 | 8 | 14169 | 28500 | 49.72%
[29 empty] | 2019 | September | 11 | 9 | 5102.5 | 28500 | 17.9%
[29 empty] | 2019 | September | 11 | 10 | 10876 | 28500 | 38.16%
[29 empty] | 2019 | September | 11 | 11 | 13182.5 | 28500 | 46.25%
[29 empty] | 2019 | September | 11 | 12 | 5052.5 | 28500 | 17.73%
[29 empty] | 2019 | September | 11 | 13 | 5877.5 | 28500 | 20.62%
[29 empty] | 2019 | September | 11 | 14 | 2459 | 28500 | 8.628%
[29 empty] | 2019 | September | 11 | 15 | 2531 | 28500 | 8.881%
[29 empty] | 2019 | September | 11 | 16 | 3862 | 28500 | 13.55%
[29 empty] | 2019 | September | 11 | 17 | 3438 | 28500 | 12.06%
[29 empty] | 2019 | September | 11 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 11 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 11 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 11 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 11 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 11 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 12 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 12 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 12 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 12 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 12 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 12 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 12 | 6 | 1101 | 28500 | 3.863%
[29 empty] | 2019 | September | 12 | 7 | 4479.5 | 28500 | 15.72%
[29 empty] | 2019 | September | 12 | 8 | 19201.5 | 28500 | 67.37%
[29 empty] | 2019 | September | 12 | 9 | 13458.5 | 28500 | 47.22%
[29 empty] | 2019 | September | 12 | 10 | 6631 | 28500 | 23.27%
[29 empty] | 2019 | September | 12 | 11 | 8486 | 28500 | 29.78%
[29 empty] | 2019 | September | 12 | 12 | 18052 | 28500 | 63.34%
[29 empty] | 2019 | September | 12 | 13 | 34316.5 | 28500 | 120.4%
[29 empty] | 2019 | September | 12 | 14 | 27478 | 28500 | 96.41%
[29 empty] | 2019 | September | 12 | 15 | 17635.5 | 28500 | 61.88%
[29 empty] | 2019 | September | 12 | 16 | 11374.5 | 28500 | 39.91%
[29 empty] | 2019 | September | 12 | 17 | 4076 | 28500 | 14.3%
[29 empty] | 2019 | September | 12 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 12 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 12 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 12 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 12 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 12 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 13 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 13 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 13 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 13 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 13 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 13 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 13 | 6 | 874 | 28500 | 3.067%
[29 empty] | 2019 | September | 13 | 7 | 9800.5 | 28500 | 34.39%
[29 empty] | 2019 | September | 13 | 8 | 19845.5 | 28500 | 69.63%
[29 empty] | 2019 | September | 13 | 9 | 27856 | 28500 | 97.74%
[29 empty] | 2019 | September | 13 | 10 | 35040.5 | 28500 | 122.9%
[29 empty] | 2019 | September | 13 | 11 | 38127 | 28500 | 133.8%
[29 empty] | 2019 | September | 13 | 12 | 37750.5 | 28500 | 132.5%
[29 empty] | 2019 | September | 13 | 13 | 36923 | 28500 | 129.6%
[29 empty] | 2019 | September | 13 | 14 | 32203.5 | 28500 | 113%
[29 empty] | 2019 | September | 13 | 15 | 25001 | 28500 | 87.72%
[29 empty] | 2019 | September | 13 | 16 | 14927.5 | 28500 | 52.38%
[29 empty] | 2019 | September | 13 | 17 | 4558.5 | 28500 | 15.99%
[29 empty] | 2019 | September | 13 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 13 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 13 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 13 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 13 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 13 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 14 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 14 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 14 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 14 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 14 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 14 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 14 | 6 | 892 | 28500 | 3.13%
[29 empty] | 2019 | September | 14 | 7 | 9690.5 | 28500 | 34%
[29 empty] | 2019 | September | 14 | 8 | 18795 | 28500 | 65.95%
[29 empty] | 2019 | September | 14 | 9 | 28203.5 | 28500 | 98.96%
[29 empty] | 2019 | September | 14 | 10 | 33459.5 | 28500 | 117.4%
[29 empty] | 2019 | September | 14 | 11 | 35507 | 28500 | 124.6%
[29 empty] | 2019 | September | 14 | 12 | 36403 | 28500 | 127.7%
[29 empty] | 2019 | September | 14 | 13 | 35249.5 | 28500 | 123.7%
[29 empty] | 2019 | September | 14 | 14 | 30031 | 28500 | 105.4%
[29 empty] | 2019 | September | 14 | 15 | 23578 | 28500 | 82.73%
[29 empty] | 2019 | September | 14 | 16 | 13557 | 28500 | 47.57%
[29 empty] | 2019 | September | 14 | 17 | 3431.5 | 28500 | 12.04%
[29 empty] | 2019 | September | 14 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 14 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 14 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 14 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 14 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 14 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 15 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 15 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 15 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 15 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 15 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 15 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 15 | 6 | 611.5 | 28500 | 2.146%
[29 empty] | 2019 | September | 15 | 7 | 7873.5 | 28500 | 27.63%
[29 empty] | 2019 | September | 15 | 8 | 19060.5 | 28500 | 66.88%
[29 empty] | 2019 | September | 15 | 9 | 27707.5 | 28500 | 97.22%
[29 empty] | 2019 | September | 15 | 10 | 32885 | 28500 | 115.4%
[29 empty] | 2019 | September | 15 | 11 | 35051 | 28500 | 123%
[29 empty] | 2019 | September | 15 | 12 | 35763 | 28500 | 125.5%
[29 empty] | 2019 | September | 15 | 13 | 34327.5 | 28500 | 120.4%
[29 empty] | 2019 | September | 15 | 14 | 30168.5 | 28500 | 105.9%
[29 empty] | 2019 | September | 15 | 15 | 19485 | 28500 | 68.37%
[29 empty] | 2019 | September | 15 | 16 | 13427.5 | 28500 | 47.11%
[29 empty] | 2019 | September | 15 | 17 | 3949.5 | 28500 | 13.86%
[29 empty] | 2019 | September | 15 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 15 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 15 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 15 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 15 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 15 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 16 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 16 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 16 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 16 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 16 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 16 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 16 | 6 | 69.5 | 28500 | 0.2439%
[29 empty] | 2019 | September | 16 | 7 | 1974.5 | 28500 | 6.928%
[29 empty] | 2019 | September | 16 | 8 | 3094 | 28500 | 10.86%
[29 empty] | 2019 | September | 16 | 9 | 5515 | 28500 | 19.35%
[29 empty] | 2019 | September | 16 | 10 | 9557 | 28500 | 33.53%
[29 empty] | 2019 | September | 16 | 11 | 7768.5 | 28500 | 27.26%
[29 empty] | 2019 | September | 16 | 12 | 4108.5 | 28500 | 14.42%
[29 empty] | 2019 | September | 16 | 13 | 5814 | 28500 | 20.4%
[29 empty] | 2019 | September | 16 | 14 | 3770.5 | 28500 | 13.23%
[29 empty] | 2019 | September | 16 | 15 | 2441.5 | 28500 | 8.567%
[29 empty] | 2019 | September | 16 | 16 | 803 | 28500 | 2.818%
[29 empty] | 2019 | September | 16 | 17 | 1322 | 28500 | 4.639%
[29 empty] | 2019 | September | 16 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 16 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 16 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 16 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 16 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 16 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 17 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 17 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 17 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 17 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 17 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 17 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 17 | 6 | 594 | 28500 | 2.084%
[29 empty] | 2019 | September | 17 | 7 | 9286 | 28500 | 32.58%
[29 empty] | 2019 | September | 17 | 8 | 20393 | 28500 | 71.55%
[29 empty] | 2019 | September | 17 | 9 | 28592.5 | 28500 | 100.3%
[29 empty] | 2019 | September | 17 | 10 | 34274 | 28500 | 120.3%
[29 empty] | 2019 | September | 17 | 11 | 36939.5 | 28500 | 129.6%
[29 empty] | 2019 | September | 17 | 12 | 37475 | 28500 | 131.5%
[29 empty] | 2019 | September | 17 | 13 | 36129 | 28500 | 126.8%
[29 empty] | 2019 | September | 17 | 14 | 31728 | 28500 | 111.3%
[29 empty] | 2019 | September | 17 | 15 | 24492 | 28500 | 85.94%
[29 empty] | 2019 | September | 17 | 16 | 14236.5 | 28500 | 49.95%
[29 empty] | 2019 | September | 17 | 17 | 3548.5 | 28500 | 12.45%
[29 empty] | 2019 | September | 17 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 17 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 17 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 17 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 17 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 17 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 18 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 18 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 18 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 18 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 18 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 18 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 18 | 6 | 689 | 28500 | 2.418%
[29 empty] | 2019 | September | 18 | 7 | 9390.5 | 28500 | 32.95%
[29 empty] | 2019 | September | 18 | 8 | 20135 | 28500 | 70.65%
[29 empty] | 2019 | September | 18 | 9 | 28312.5 | 28500 | 99.34%
[29 empty] | 2019 | September | 18 | 10 | 33982.5 | 28500 | 119.2%
[29 empty] | 2019 | September | 18 | 11 | 36324.5 | 28500 | 127.5%
[29 empty] | 2019 | September | 18 | 12 | 37073 | 28500 | 130.1%
[29 empty] | 2019 | September | 18 | 13 | 35671 | 28500 | 125.2%
[29 empty] | 2019 | September | 18 | 14 | 31038.5 | 28500 | 108.9%
[29 empty] | 2019 | September | 18 | 15 | 23698 | 28500 | 83.15%
[29 empty] | 2019 | September | 18 | 16 | 13881 | 28500 | 48.71%
[29 empty] | 2019 | September | 18 | 17 | 3391 | 28500 | 11.9%
[29 empty] | 2019 | September | 18 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 18 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 18 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 18 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 18 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 18 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 19 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 19 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 19 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 19 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 19 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 19 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 19 | 6 | 601.5 | 28500 | 2.111%
[29 empty] | 2019 | September | 19 | 7 | 8795 | 28500 | 30.86%
[29 empty] | 2019 | September | 19 | 8 | 18963 | 28500 | 66.54%
[29 empty] | 2019 | September | 19 | 9 | 26970 | 28500 | 94.63%
[29 empty] | 2019 | September | 19 | 10 | 32731 | 28500 | 114.8%
[29 empty] | 2019 | September | 19 | 11 | 35250 | 28500 | 123.7%
[29 empty] | 2019 | September | 19 | 12 | 35579.5 | 28500 | 124.8%
[29 empty] | 2019 | September | 19 | 13 | 34352 | 28500 | 120.5%
[29 empty] | 2019 | September | 19 | 14 | 29999 | 28500 | 105.3%
[29 empty] | 2019 | September | 19 | 15 | 22959 | 28500 | 80.56%
[29 empty] | 2019 | September | 19 | 16 | 13180 | 28500 | 46.25%
[29 empty] | 2019 | September | 19 | 17 | 3119.5 | 28500 | 10.95%
[29 empty] | 2019 | September | 19 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 19 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 19 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 19 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 19 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 19 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 20 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 20 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 20 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 20 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 20 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 20 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 20 | 6 | 529.5 | 28500 | 1.858%
[29 empty] | 2019 | September | 20 | 7 | 9283 | 28500 | 32.57%
[29 empty] | 2019 | September | 20 | 8 | 20015.5 | 28500 | 70.23%
[29 empty] | 2019 | September | 20 | 9 | 28370 | 28500 | 99.54%
[29 empty] | 2019 | September | 20 | 10 | 35033 | 28500 | 122.9%
[29 empty] | 2019 | September | 20 | 11 | 36864.5 | 28500 | 129.3%
[29 empty] | 2019 | September | 20 | 12 | 37616 | 28500 | 132%
[29 empty] | 2019 | September | 20 | 13 | 36116 | 28500 | 126.7%
[29 empty] | 2019 | September | 20 | 14 | 31286.5 | 28500 | 109.8%
[29 empty] | 2019 | September | 20 | 15 | 23601 | 28500 | 82.81%
[29 empty] | 2019 | September | 20 | 16 | 13494.5 | 28500 | 47.35%
[29 empty] | 2019 | September | 20 | 17 | 2956.5 | 28500 | 10.37%
[29 empty] | 2019 | September | 20 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 20 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 20 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 20 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 20 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 20 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 21 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 21 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 21 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 21 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 21 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 21 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 21 | 6 | 444 | 28500 | 1.558%
[29 empty] | 2019 | September | 21 | 7 | 8882.5 | 28500 | 31.17%
[29 empty] | 2019 | September | 21 | 8 | 19590.5 | 28500 | 68.74%
[29 empty] | 2019 | September | 21 | 9 | 27741.5 | 28500 | 97.34%
[29 empty] | 2019 | September | 21 | 10 | 33278 | 28500 | 116.8%
[29 empty] | 2019 | September | 21 | 11 | 35752.5 | 28500 | 125.4%
[29 empty] | 2019 | September | 21 | 12 | 36325.5 | 28500 | 127.5%
[29 empty] | 2019 | September | 21 | 13 | 34771 | 28500 | 122%
[29 empty] | 2019 | September | 21 | 14 | 30011.5 | 28500 | 105.3%
[29 empty] | 2019 | September | 21 | 15 | 22258 | 28500 | 78.1%
[29 empty] | 2019 | September | 21 | 16 | 12547 | 28500 | 44.02%
[29 empty] | 2019 | September | 21 | 17 | 2769.5 | 28500 | 9.718%
[29 empty] | 2019 | September | 21 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 21 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 21 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 21 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 21 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 21 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 22 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 22 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 22 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 22 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 22 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 22 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 22 | 6 | 112 | 28500 | 0.393%
[29 empty] | 2019 | September | 22 | 7 | 3664 | 28500 | 12.86%
[29 empty] | 2019 | September | 22 | 8 | 5524 | 28500 | 19.38%
[29 empty] | 2019 | September | 22 | 9 | 21052 | 28500 | 73.87%
[29 empty] | 2019 | September | 22 | 10 | 23341.5 | 28500 | 81.9%
[29 empty] | 2019 | September | 22 | 11 | 6603.5 | 28500 | 23.17%
[29 empty] | 2019 | September | 22 | 12 | 1808 | 28500 | 6.344%
[29 empty] | 2019 | September | 22 | 13 | 7156 | 28500 | 25.11%
[29 empty] | 2019 | September | 22 | 14 | 3810.5 | 28500 | 13.37%
[29 empty] | 2019 | September | 22 | 15 | 2623.5 | 28500 | 9.205%
[29 empty] | 2019 | September | 22 | 16 | 996.5 | 28500 | 3.496%
[29 empty] | 2019 | September | 22 | 17 | 184 | 28500 | 0.6456%
[29 empty] | 2019 | September | 22 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 22 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 22 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 22 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 22 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 22 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 23 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 23 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 23 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 23 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 23 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 23 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 23 | 6 | 320.5 | 28500 | 1.125%
[29 empty] | 2019 | September | 23 | 7 | 8740 | 28500 | 30.67%
[29 empty] | 2019 | September | 23 | 8 | 19436.5 | 28500 | 68.2%
[29 empty] | 2019 | September | 23 | 9 | 27376 | 28500 | 96.06%
[29 empty] | 2019 | September | 23 | 10 | 15464.5 | 28500 | 54.26%
[29 empty] | 2019 | September | 23 | 11 | 6512 | 28500 | 22.85%
[29 empty] | 2019 | September | 23 | 12 | 8382 | 28500 | 29.41%
[29 empty] | 2019 | September | 23 | 13 | 27941 | 28500 | 98.04%
[29 empty] | 2019 | September | 23 | 14 | 3889.5 | 28500 | 13.65%
[29 empty] | 2019 | September | 23 | 15 | 2764.5 | 28500 | 9.7%
[29 empty] | 2019 | September | 23 | 16 | 401 | 28500 | 1.407%
[29 empty] | 2019 | September | 23 | 17 | 403.5 | 28500 | 1.416%
[29 empty] | 2019 | September | 23 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 23 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 23 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 23 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 23 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 23 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 24 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 24 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 24 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 24 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 24 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 24 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 24 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 24 | 7 | 348 | 28500 | 1.221%
[29 empty] | 2019 | September | 24 | 8 | 907.5 | 28500 | 3.184%
[29 empty] | 2019 | September | 24 | 9 | 2836 | 28500 | 9.951%
[29 empty] | 2019 | September | 24 | 10 | 13607 | 28500 | 47.74%
[29 empty] | 2019 | September | 24 | 11 | 12854 | 28500 | 45.1%
[29 empty] | 2019 | September | 24 | 12 | 6690.5 | 28500 | 23.48%
[29 empty] | 2019 | September | 24 | 13 | 24940.5 | 28500 | 87.51%
[29 empty] | 2019 | September | 24 | 14 | 17417.5 | 28500 | 61.11%
[29 empty] | 2019 | September | 24 | 15 | 20176 | 28500 | 70.79%
[29 empty] | 2019 | September | 24 | 16 | 769 | 28500 | 2.698%
[29 empty] | 2019 | September | 24 | 17 | 1093 | 28500 | 3.835%
[29 empty] | 2019 | September | 24 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 24 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 24 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 24 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 24 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 24 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 25 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 25 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 25 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 25 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 25 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 25 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 25 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 25 | 7 | 4777 | 28500 | 16.76%
[29 empty] | 2019 | September | 25 | 8 | 5063.5 | 28500 | 17.77%
[29 empty] | 2019 | September | 25 | 9 | 2316.5 | 28500 | 8.128%
[29 empty] | 2019 | September | 25 | 10 | 9500 | 28500 | 33.33%
[29 empty] | 2019 | September | 25 | 11 | 14622 | 28500 | 51.31%
[29 empty] | 2019 | September | 25 | 12 | 12148.5 | 28500 | 42.63%
[29 empty] | 2019 | September | 25 | 13 | 6295.5 | 28500 | 22.09%
[29 empty] | 2019 | September | 25 | 14 | 21840 | 28500 | 76.63%
[29 empty] | 2019 | September | 25 | 15 | 16713.5 | 28500 | 58.64%
[29 empty] | 2019 | September | 25 | 16 | 11511 | 28500 | 40.39%
[29 empty] | 2019 | September | 25 | 17 | 1503 | 28500 | 5.274%
[29 empty] | 2019 | September | 25 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 25 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 25 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 25 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 25 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 25 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 26 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 26 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 26 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 26 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 26 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 26 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 26 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 26 | 7 | 2314 | 28500 | 8.119%
[29 empty] | 2019 | September | 26 | 8 | 4250 | 28500 | 14.91%
[29 empty] | 2019 | September | 26 | 9 | 5579.5 | 28500 | 19.58%
[29 empty] | 2019 | September | 26 | 10 | 11694.5 | 28500 | 41.03%
[29 empty] | 2019 | September | 26 | 11 | 12043.5 | 28500 | 42.26%
[29 empty] | 2019 | September | 26 | 12 | 31877.5 | 28500 | 111.9%
[29 empty] | 2019 | September | 26 | 13 | 11199.5 | 28500 | 39.3%
[29 empty] | 2019 | September | 26 | 14 | 14907 | 28500 | 52.31%
[29 empty] | 2019 | September | 26 | 15 | 19990 | 28500 | 70.14%
[29 empty] | 2019 | September | 26 | 16 | 10439 | 28500 | 36.63%
[29 empty] | 2019 | September | 26 | 17 | 1508.5 | 28500 | 5.293%
[29 empty] | 2019 | September | 26 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 26 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 26 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 26 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 26 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 26 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 27 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 27 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 27 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 27 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 27 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 27 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 27 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 27 | 7 | 7409 | 28500 | 26%
[29 empty] | 2019 | September | 27 | 8 | 20297 | 28500 | 71.22%
[29 empty] | 2019 | September | 27 | 9 | 17926 | 28500 | 62.9%
[29 empty] | 2019 | September | 27 | 10 | 12810 | 28500 | 44.95%
[29 empty] | 2019 | September | 27 | 11 | 2427.5 | 28500 | 8.518%
[29 empty] | 2019 | September | 27 | 12 | 13112 | 28500 | 46.01%
[29 empty] | 2019 | September | 27 | 13 | 11839 | 28500 | 41.54%
[29 empty] | 2019 | September | 27 | 14 | 2732.5 | 28500 | 9.588%
[29 empty] | 2019 | September | 27 | 15 | 15322 | 28500 | 53.76%
[29 empty] | 2019 | September | 27 | 16 | 8950 | 28500 | 31.4%
[29 empty] | 2019 | September | 27 | 17 | 393.5 | 28500 | 1.381%
[29 empty] | 2019 | September | 27 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 27 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 27 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 27 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 27 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 27 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 28 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 28 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 28 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 28 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 28 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 28 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 28 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 28 | 7 | 5466 | 28500 | 19.18%
[29 empty] | 2019 | September | 28 | 8 | 11032.5 | 28500 | 38.71%
[29 empty] | 2019 | September | 28 | 9 | 6850.5 | 28500 | 24.04%
[29 empty] | 2019 | September | 28 | 10 | 23856.5 | 28500 | 83.71%
[29 empty] | 2019 | September | 28 | 11 | 15971.5 | 28500 | 56.04%
[29 empty] | 2019 | September | 28 | 12 | 11679.5 | 28500 | 40.98%
[29 empty] | 2019 | September | 28 | 13 | 5364 | 28500 | 18.82%
[29 empty] | 2019 | September | 28 | 14 | 3605 | 28500 | 12.65%
[29 empty] | 2019 | September | 28 | 15 | 8918 | 28500 | 31.29%
[29 empty] | 2019 | September | 28 | 16 | 1982 | 28500 | 6.954%
[29 empty] | 2019 | September | 28 | 17 | 721 | 28500 | 2.53%
[29 empty] | 2019 | September | 28 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 28 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 28 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 28 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 28 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 28 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 29 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 29 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 29 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 29 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 29 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 29 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 29 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 29 | 7 | 524.5 | 28500 | 1.84%
[29 empty] | 2019 | September | 29 | 8 | 2996.5 | 28500 | 10.51%
[29 empty] | 2019 | September | 29 | 9 | 1949.5 | 28500 | 6.84%
[29 empty] | 2019 | September | 29 | 10 | 2279 | 28500 | 7.996%
[29 empty] | 2019 | September | 29 | 11 | 3474 | 28500 | 12.19%
[29 empty] | 2019 | September | 29 | 12 | 6031.5 | 28500 | 21.16%
[29 empty] | 2019 | September | 29 | 13 | 4047.5 | 28500 | 14.2%
[29 empty] | 2019 | September | 29 | 14 | 12855.5 | 28500 | 45.11%
[29 empty] | 2019 | September | 29 | 15 | 5977 | 28500 | 20.97%
[29 empty] | 2019 | September | 29 | 16 | 1949 | 28500 | 6.839%
[29 empty] | 2019 | September | 29 | 17 | 237.5 | 28500 | 0.8333%
[29 empty] | 2019 | September | 29 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 29 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 29 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 29 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 29 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 29 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 30 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 30 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 30 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 30 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 30 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 30 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 30 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 30 | 7 | 387.5 | 28500 | 1.36%
[29 empty] | 2019 | September | 30 | 8 | 10418 | 28500 | 36.55%
[29 empty] | 2019 | September | 30 | 9 | 14370.5 | 28500 | 50.42%
[29 empty] | 2019 | September | 30 | 10 | 12722 | 28500 | 44.64%
[29 empty] | 2019 | September | 30 | 11 | 10679 | 28500 | 37.47%
[29 empty] | 2019 | September | 30 | 12 | 11013 | 28500 | 38.64%
[29 empty] | 2019 | September | 30 | 13 | 3132.5 | 28500 | 10.99%
[29 empty] | 2019 | September | 30 | 14 | 2651 | 28500 | 9.302%
[29 empty] | 2019 | September | 30 | 15 | 556.5 | 28500 | 1.953%
[29 empty] | 2019 | September | 30 | 16 | 1392 | 28500 | 4.884%
[29 empty] | 2019 | September | 30 | 17 | 92 | 28500 | 0.3228%
[29 empty] | 2019 | September | 30 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 30 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 30 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 30 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 30 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | September | 30 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 1 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 1 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 1 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 1 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 1 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 1 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 1 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 1 | 7 | 5978 | 28500 | 20.98%
[29 empty] | 2019 | October | 1 | 8 | 16506.5 | 28500 | 57.92%
[29 empty] | 2019 | October | 1 | 9 | 7088 | 28500 | 24.87%
[29 empty] | 2019 | October | 1 | 10 | 1099.5 | 28500 | 3.858%
[29 empty] | 2019 | October | 1 | 11 | 10747 | 28500 | 37.71%
[29 empty] | 2019 | October | 1 | 12 | 23327 | 28500 | 81.85%
[29 empty] | 2019 | October | 1 | 13 | 32594.5 | 28500 | 114.4%
[29 empty] | 2019 | October | 1 | 14 | 16598 | 28500 | 58.24%
[29 empty] | 2019 | October | 1 | 15 | 7768 | 28500 | 27.26%
[29 empty] | 2019 | October | 1 | 16 | 972.5 | 28500 | 3.412%
[29 empty] | 2019 | October | 1 | 17 | 544 | 28500 | 1.909%
[29 empty] | 2019 | October | 1 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 1 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 1 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 1 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 1 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 1 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 2 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 2 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 2 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 2 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 2 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 2 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 2 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 2 | 7 | 8607.5 | 28500 | 30.2%
[29 empty] | 2019 | October | 2 | 8 | 20134.5 | 28500 | 70.65%
[29 empty] | 2019 | October | 2 | 9 | 28690 | 28500 | 100.7%
[29 empty] | 2019 | October | 2 | 10 | 34843.5 | 28500 | 122.3%
[29 empty] | 2019 | October | 2 | 11 | 36757 | 28500 | 129%
[29 empty] | 2019 | October | 2 | 12 | 15898.5 | 28500 | 55.78%
[29 empty] | 2019 | October | 2 | 13 | 12859 | 28500 | 45.12%
[29 empty] | 2019 | October | 2 | 14 | 26464 | 28500 | 92.86%
[29 empty] | 2019 | October | 2 | 15 | 19760 | 28500 | 69.33%
[29 empty] | 2019 | October | 2 | 16 | 11536.5 | 28500 | 40.48%
[29 empty] | 2019 | October | 2 | 17 | 512.5 | 28500 | 1.798%
[29 empty] | 2019 | October | 2 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 2 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 2 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 2 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 2 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 2 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 3 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 3 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 3 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 3 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 3 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 3 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 3 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 3 | 7 | 3364 | 28500 | 11.8%
[29 empty] | 2019 | October | 3 | 8 | 6944 | 28500 | 24.36%
[29 empty] | 2019 | October | 3 | 9 | 10307 | 28500 | 36.16%
[29 empty] | 2019 | October | 3 | 10 | 6310.5 | 28500 | 22.14%
[29 empty] | 2019 | October | 3 | 11 | 6440 | 28500 | 22.6%
[29 empty] | 2019 | October | 3 | 12 | 2923.5 | 28500 | 10.26%
[29 empty] | 2019 | October | 3 | 13 | 2169 | 28500 | 7.611%
[29 empty] | 2019 | October | 3 | 14 | 4815 | 28500 | 16.89%
[29 empty] | 2019 | October | 3 | 15 | 3686 | 28500 | 12.93%
[29 empty] | 2019 | October | 3 | 16 | 1471.5 | 28500 | 5.163%
[29 empty] | 2019 | October | 3 | 17 | 170 | 28500 | 0.5965%
[29 empty] | 2019 | October | 3 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 3 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 3 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 3 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 3 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 3 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 4 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 4 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 4 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 4 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 4 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 4 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 4 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 4 | 7 | 6727 | 28500 | 23.6%
[29 empty] | 2019 | October | 4 | 8 | 4634.5 | 28500 | 16.26%
[29 empty] | 2019 | October | 4 | 9 | 1579 | 28500 | 5.54%
[29 empty] | 2019 | October | 4 | 10 | 5467 | 28500 | 19.18%
[29 empty] | 2019 | October | 4 | 11 | 9297 | 28500 | 32.62%
[29 empty] | 2019 | October | 4 | 12 | 2751.5 | 28500 | 9.654%
[29 empty] | 2019 | October | 4 | 13 | 16996 | 28500 | 59.64%
[29 empty] | 2019 | October | 4 | 14 | 4643.5 | 28500 | 16.29%
[29 empty] | 2019 | October | 4 | 15 | 11411.5 | 28500 | 40.04%
[29 empty] | 2019 | October | 4 | 16 | 6182 | 28500 | 21.69%
[29 empty] | 2019 | October | 4 | 17 | 151 | 28500 | 0.5298%
[29 empty] | 2019 | October | 4 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 4 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 4 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 4 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 4 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 4 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 5 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 5 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 5 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 5 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 5 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 5 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 5 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 5 | 7 | 3248.5 | 28500 | 11.4%
[29 empty] | 2019 | October | 5 | 8 | 5356 | 28500 | 18.79%
[29 empty] | 2019 | October | 5 | 9 | 2158.5 | 28500 | 7.574%
[29 empty] | 2019 | October | 5 | 10 | 7853.5 | 28500 | 27.56%
[29 empty] | 2019 | October | 5 | 11 | 5855 | 28500 | 20.54%
[29 empty] | 2019 | October | 5 | 12 | 5696 | 28500 | 19.99%
[29 empty] | 2019 | October | 5 | 13 | 9612.5 | 28500 | 33.73%
[29 empty] | 2019 | October | 5 | 14 | 2036.5 | 28500 | 7.146%
[29 empty] | 2019 | October | 5 | 15 | 3429 | 28500 | 12.03%
[29 empty] | 2019 | October | 5 | 16 | 2220 | 28500 | 7.789%
[29 empty] | 2019 | October | 5 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 5 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 5 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 5 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 5 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 5 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 5 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 6 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 6 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 6 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 6 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 6 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 6 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 6 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 6 | 7 | 4577.5 | 28500 | 16.06%
[29 empty] | 2019 | October | 6 | 8 | 9378.5 | 28500 | 32.91%
[29 empty] | 2019 | October | 6 | 9 | 17470 | 28500 | 61.3%
[29 empty] | 2019 | October | 6 | 10 | 3706 | 28500 | 13%
[29 empty] | 2019 | October | 6 | 11 | 11296.5 | 28500 | 39.64%
[29 empty] | 2019 | October | 6 | 12 | 14339.5 | 28500 | 50.31%
[29 empty] | 2019 | October | 6 | 13 | 29246.5 | 28500 | 102.6%
[29 empty] | 2019 | October | 6 | 14 | 27683 | 28500 | 97.13%
[29 empty] | 2019 | October | 6 | 15 | 6361.5 | 28500 | 22.32%
[29 empty] | 2019 | October | 6 | 16 | 1788 | 28500 | 6.274%
[29 empty] | 2019 | October | 6 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 6 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 6 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 6 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 6 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 6 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 6 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 7 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 7 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 7 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 7 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 7 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 7 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 7 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 7 | 7 | 1534 | 28500 | 5.382%
[29 empty] | 2019 | October | 7 | 8 | 10808 | 28500 | 37.92%
[29 empty] | 2019 | October | 7 | 9 | 6689.5 | 28500 | 23.47%
[29 empty] | 2019 | October | 7 | 10 | 8056.5 | 28500 | 28.27%
[29 empty] | 2019 | October | 7 | 11 | 6604 | 28500 | 23.17%
[29 empty] | 2019 | October | 7 | 12 | 13975 | 28500 | 49.04%
[29 empty] | 2019 | October | 7 | 13 | 2824.5 | 28500 | 9.911%
[29 empty] | 2019 | October | 7 | 14 | 1291 | 28500 | 4.53%
[29 empty] | 2019 | October | 7 | 15 | 2194 | 28500 | 7.698%
[29 empty] | 2019 | October | 7 | 16 | 1188 | 28500 | 4.168%
[29 empty] | 2019 | October | 7 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 7 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 7 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 7 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 7 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 7 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 7 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 8 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 8 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 8 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 8 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 8 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 8 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 8 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 8 | 7 | 4705.5 | 28500 | 16.51%
[29 empty] | 2019 | October | 8 | 8 | 5089.5 | 28500 | 17.86%
[29 empty] | 2019 | October | 8 | 9 | 22877 | 28500 | 80.27%
[29 empty] | 2019 | October | 8 | 10 | 17135.5 | 28500 | 60.12%
[29 empty] | 2019 | October | 8 | 11 | 3637.5 | 28500 | 12.76%
[29 empty] | 2019 | October | 8 | 12 | 4975 | 28500 | 17.46%
[29 empty] | 2019 | October | 8 | 13 | 25235.5 | 28500 | 88.55%
[29 empty] | 2019 | October | 8 | 14 | 16838.5 | 28500 | 59.08%
[29 empty] | 2019 | October | 8 | 15 | 17097 | 28500 | 59.99%
[29 empty] | 2019 | October | 8 | 16 | 1182 | 28500 | 4.147%
[29 empty] | 2019 | October | 8 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 8 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 8 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 8 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 8 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 8 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 8 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 9 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 9 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 9 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 9 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 9 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 9 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 9 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 9 | 7 | 1302.5 | 28500 | 4.57%
[29 empty] | 2019 | October | 9 | 8 | 6877 | 28500 | 24.13%
[29 empty] | 2019 | October | 9 | 9 | 24148.5 | 28500 | 84.73%
[29 empty] | 2019 | October | 9 | 10 | 17193 | 28500 | 60.33%
[29 empty] | 2019 | October | 9 | 11 | 19468 | 28500 | 68.31%
[29 empty] | 2019 | October | 9 | 12 | 27925.5 | 28500 | 97.98%
[29 empty] | 2019 | October | 9 | 13 | 26859.5 | 28500 | 94.24%
[29 empty] | 2019 | October | 9 | 14 | 16811 | 28500 | 58.99%
[29 empty] | 2019 | October | 9 | 15 | 17350 | 28500 | 60.88%
[29 empty] | 2019 | October | 9 | 16 | 2342.5 | 28500 | 8.219%
[29 empty] | 2019 | October | 9 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 9 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 9 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 9 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 9 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 9 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 9 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 10 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 10 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 10 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 10 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 10 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 10 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 10 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 10 | 7 | 3991 | 28500 | 14%
[29 empty] | 2019 | October | 10 | 8 | 16763 | 28500 | 58.82%
[29 empty] | 2019 | October | 10 | 9 | 23154.5 | 28500 | 81.24%
[29 empty] | 2019 | October | 10 | 10 | 30331.5 | 28500 | 106.4%
[29 empty] | 2019 | October | 10 | 11 | 26776 | 28500 | 93.95%
[29 empty] | 2019 | October | 10 | 12 | 21997.5 | 28500 | 77.18%
[29 empty] | 2019 | October | 10 | 13 | 24036.5 | 28500 | 84.34%
[29 empty] | 2019 | October | 10 | 14 | 18358 | 28500 | 64.41%
[29 empty] | 2019 | October | 10 | 15 | 8445 | 28500 | 29.63%
[29 empty] | 2019 | October | 10 | 16 | 1078.5 | 28500 | 3.784%
[29 empty] | 2019 | October | 10 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 10 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 10 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 10 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 10 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 10 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 10 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 11 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 11 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 11 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 11 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 11 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 11 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 11 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 11 | 7 | 589.5 | 28500 | 2.068%
[29 empty] | 2019 | October | 11 | 8 | 1929 | 28500 | 6.768%
[29 empty] | 2019 | October | 11 | 9 | 5270 | 28500 | 18.49%
[29 empty] | 2019 | October | 11 | 10 | 3767.5 | 28500 | 13.22%
[29 empty] | 2019 | October | 11 | 11 | 3801 | 28500 | 13.34%
[29 empty] | 2019 | October | 11 | 12 | 3030 | 28500 | 10.63%
[29 empty] | 2019 | October | 11 | 13 | 3596 | 28500 | 12.62%
[29 empty] | 2019 | October | 11 | 14 | 3094 | 28500 | 10.86%
[29 empty] | 2019 | October | 11 | 15 | 2857.5 | 28500 | 10.03%
[29 empty] | 2019 | October | 11 | 16 | 1625 | 28500 | 5.702%
[29 empty] | 2019 | October | 11 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 11 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 11 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 11 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 11 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 11 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 11 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 12 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 12 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 12 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 12 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 12 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 12 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 12 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 12 | 7 | 901.5 | 28500 | 3.163%
[29 empty] | 2019 | October | 12 | 8 | 2223.5 | 28500 | 7.802%
[29 empty] | 2019 | October | 12 | 9 | 1996 | 28500 | 7.004%
[29 empty] | 2019 | October | 12 | 10 | 2817 | 28500 | 9.884%
[29 empty] | 2019 | October | 12 | 11 | 3081 | 28500 | 10.81%
[29 empty] | 2019 | October | 12 | 12 | 3231.5 | 28500 | 11.34%
[29 empty] | 2019 | October | 12 | 13 | 2810 | 28500 | 9.86%
[29 empty] | 2019 | October | 12 | 14 | 1986.5 | 28500 | 6.97%
[29 empty] | 2019 | October | 12 | 15 | 2022.5 | 28500 | 7.096%
[29 empty] | 2019 | October | 12 | 16 | 791.5 | 28500 | 2.777%
[29 empty] | 2019 | October | 12 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 12 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 12 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 12 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 12 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 12 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 12 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 13 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 13 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 13 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 13 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 13 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 13 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 13 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 13 | 7 | 12 | 28500 | 0.04211%
[29 empty] | 2019 | October | 13 | 8 | 3817 | 28500 | 13.39%
[29 empty] | 2019 | October | 13 | 9 | 2468 | 28500 | 8.66%
[29 empty] | 2019 | October | 13 | 10 | 9578 | 28500 | 33.61%
[29 empty] | 2019 | October | 13 | 11 | 2393.5 | 28500 | 8.398%
[29 empty] | 2019 | October | 13 | 12 | 4836.5 | 28500 | 16.97%
[29 empty] | 2019 | October | 13 | 13 | 11701.5 | 28500 | 41.06%
[29 empty] | 2019 | October | 13 | 14 | 2029.5 | 28500 | 7.121%
[29 empty] | 2019 | October | 13 | 15 | 15148 | 28500 | 53.15%
[29 empty] | 2019 | October | 13 | 16 | 5862.5 | 28500 | 20.57%
[29 empty] | 2019 | October | 13 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 13 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 13 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 13 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 13 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 13 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 13 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 14 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 14 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 14 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 14 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 14 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 14 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 14 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 14 | 7 | 773 | 28500 | 2.712%
[29 empty] | 2019 | October | 14 | 8 | 1411.5 | 28500 | 4.953%
[29 empty] | 2019 | October | 14 | 9 | 1695 | 28500 | 5.947%
[29 empty] | 2019 | October | 14 | 10 | 3214.5 | 28500 | 11.28%
[29 empty] | 2019 | October | 14 | 11 | 3285.5 | 28500 | 11.53%
[29 empty] | 2019 | October | 14 | 12 | 1830.5 | 28500 | 6.423%
[29 empty] | 2019 | October | 14 | 13 | 2307.5 | 28500 | 8.096%
[29 empty] | 2019 | October | 14 | 14 | 1359.5 | 28500 | 4.77%
[29 empty] | 2019 | October | 14 | 15 | 6420 | 28500 | 22.53%
[29 empty] | 2019 | October | 14 | 16 | 1260 | 28500 | 4.421%
[29 empty] | 2019 | October | 14 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 14 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 14 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 14 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 14 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 14 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 14 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 15 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 15 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 15 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 15 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 15 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 15 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 15 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 15 | 7 | 877 | 28500 | 3.077%
[29 empty] | 2019 | October | 15 | 8 | 4822.5 | 28500 | 16.92%
[29 empty] | 2019 | October | 15 | 9 | 8844 | 28500 | 31.03%
[29 empty] | 2019 | October | 15 | 10 | 15035.5 | 28500 | 52.76%
[29 empty] | 2019 | October | 15 | 11 | 11968.5 | 28500 | 41.99%
[29 empty] | 2019 | October | 15 | 12 | 24860 | 28500 | 87.23%
[29 empty] | 2019 | October | 15 | 13 | 16528 | 28500 | 57.99%
[29 empty] | 2019 | October | 15 | 14 | 5776 | 28500 | 20.27%
[29 empty] | 2019 | October | 15 | 15 | 9474 | 28500 | 33.24%
[29 empty] | 2019 | October | 15 | 16 | 5995 | 28500 | 21.04%
[29 empty] | 2019 | October | 15 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 15 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 15 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 15 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 15 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 15 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 15 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 16 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 16 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 16 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 16 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 16 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 16 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 16 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 16 | 7 | 163.5 | 28500 | 0.5737%
[29 empty] | 2019 | October | 16 | 8 | 1748.5 | 28500 | 6.135%
[29 empty] | 2019 | October | 16 | 9 | 5683 | 28500 | 19.94%
[29 empty] | 2019 | October | 16 | 10 | 7281 | 28500 | 25.55%
[29 empty] | 2019 | October | 16 | 11 | 13076 | 28500 | 45.88%
[29 empty] | 2019 | October | 16 | 12 | 20593.5 | 28500 | 72.26%
[29 empty] | 2019 | October | 16 | 13 | 21134 | 28500 | 74.15%
[29 empty] | 2019 | October | 16 | 14 | 6021.5 | 28500 | 21.13%
[29 empty] | 2019 | October | 16 | 15 | 12263 | 28500 | 43.03%
[29 empty] | 2019 | October | 16 | 16 | 1710.5 | 28500 | 6.002%
[29 empty] | 2019 | October | 16 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 16 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 16 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 16 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 16 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 16 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 16 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 17 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 17 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 17 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 17 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 17 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 17 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 17 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 17 | 7 | 4205.5 | 28500 | 14.76%
[29 empty] | 2019 | October | 17 | 8 | 15352.5 | 28500 | 53.87%
[29 empty] | 2019 | October | 17 | 9 | 23996.5 | 28500 | 84.2%
[29 empty] | 2019 | October | 17 | 10 | 6482 | 28500 | 22.74%
[29 empty] | 2019 | October | 17 | 11 | 15012 | 28500 | 52.67%
[29 empty] | 2019 | October | 17 | 12 | 8581.5 | 28500 | 30.11%
[29 empty] | 2019 | October | 17 | 13 | 1833 | 28500 | 6.432%
[29 empty] | 2019 | October | 17 | 14 | 3077 | 28500 | 10.8%
[29 empty] | 2019 | October | 17 | 15 | 17200.5 | 28500 | 60.35%
[29 empty] | 2019 | October | 17 | 16 | 694 | 28500 | 2.435%
[29 empty] | 2019 | October | 17 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 17 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 17 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 17 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 17 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 17 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 17 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 18 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 18 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 18 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 18 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 18 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 18 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 18 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 18 | 7 | 696 | 28500 | 2.442%
[29 empty] | 2019 | October | 18 | 8 | 14144.5 | 28500 | 49.63%
[29 empty] | 2019 | October | 18 | 9 | 25612.5 | 28500 | 89.87%
[29 empty] | 2019 | October | 18 | 10 | 30934 | 28500 | 108.5%
[29 empty] | 2019 | October | 18 | 11 | 31304 | 28500 | 109.8%
[29 empty] | 2019 | October | 18 | 12 | 29636 | 28500 | 104%
[29 empty] | 2019 | October | 18 | 13 | 19405 | 28500 | 68.09%
[29 empty] | 2019 | October | 18 | 14 | 19293 | 28500 | 67.69%
[29 empty] | 2019 | October | 18 | 15 | 4254 | 28500 | 14.93%
[29 empty] | 2019 | October | 18 | 16 | 116.5 | 28500 | 0.4088%
[29 empty] | 2019 | October | 18 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 18 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 18 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 18 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 18 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 18 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 18 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 19 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 19 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 19 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 19 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 19 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 19 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 19 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 19 | 7 | 5324.5 | 28500 | 18.68%
[29 empty] | 2019 | October | 19 | 8 | 17090.5 | 28500 | 59.97%
[29 empty] | 2019 | October | 19 | 9 | 25837 | 28500 | 90.66%
[29 empty] | 2019 | October | 19 | 10 | 32440.5 | 28500 | 113.8%
[29 empty] | 2019 | October | 19 | 11 | 30980.5 | 28500 | 108.7%
[29 empty] | 2019 | October | 19 | 12 | 13074.5 | 28500 | 45.88%
[29 empty] | 2019 | October | 19 | 13 | 20081 | 28500 | 70.46%
[29 empty] | 2019 | October | 19 | 14 | 22967 | 28500 | 80.59%
[29 empty] | 2019 | October | 19 | 15 | 13907.5 | 28500 | 48.8%
[29 empty] | 2019 | October | 19 | 16 | 1481 | 28500 | 5.196%
[29 empty] | 2019 | October | 19 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 19 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 19 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 19 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 19 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 19 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 19 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 20 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 20 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 20 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 20 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 20 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 20 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 20 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 20 | 7 | 3869.5 | 28500 | 13.58%
[29 empty] | 2019 | October | 20 | 8 | 18566.5 | 28500 | 65.15%
[29 empty] | 2019 | October | 20 | 9 | 26160.5 | 28500 | 91.79%
[29 empty] | 2019 | October | 20 | 10 | 24845.5 | 28500 | 87.18%
[29 empty] | 2019 | October | 20 | 11 | 16451.5 | 28500 | 57.72%
[29 empty] | 2019 | October | 20 | 12 | 11593 | 28500 | 40.68%
[29 empty] | 2019 | October | 20 | 13 | 8997 | 28500 | 31.57%
[29 empty] | 2019 | October | 20 | 14 | 2027 | 28500 | 7.112%
[29 empty] | 2019 | October | 20 | 15 | 2065 | 28500 | 7.246%
[29 empty] | 2019 | October | 20 | 16 | 1448 | 28500 | 5.081%
[29 empty] | 2019 | October | 20 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 20 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 20 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 20 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 20 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 20 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 20 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 21 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 21 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 21 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 21 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 21 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 21 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 21 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 21 | 7 | 1164.5 | 28500 | 4.086%
[29 empty] | 2019 | October | 21 | 8 | 1425 | 28500 | 5%
[29 empty] | 2019 | October | 21 | 9 | 8828 | 28500 | 30.98%
[29 empty] | 2019 | October | 21 | 10 | 10480 | 28500 | 36.77%
[29 empty] | 2019 | October | 21 | 11 | 4487.5 | 28500 | 15.75%
[29 empty] | 2019 | October | 21 | 12 | 5330.5 | 28500 | 18.7%
[29 empty] | 2019 | October | 21 | 13 | 5323 | 28500 | 18.68%
[29 empty] | 2019 | October | 21 | 14 | 1809.5 | 28500 | 6.349%
[29 empty] | 2019 | October | 21 | 15 | 386 | 28500 | 1.354%
[29 empty] | 2019 | October | 21 | 16 | 733.5 | 28500 | 2.574%
[29 empty] | 2019 | October | 21 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 21 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 21 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 21 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 21 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 21 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 21 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 22 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 22 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 22 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 22 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 22 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 22 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 22 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 22 | 7 | 2987.5 | 28500 | 10.48%
[29 empty] | 2019 | October | 22 | 8 | 12242.5 | 28500 | 42.96%
[29 empty] | 2019 | October | 22 | 9 | 24511 | 28500 | 86%
[29 empty] | 2019 | October | 22 | 10 | 30352 | 28500 | 106.5%
[29 empty] | 2019 | October | 22 | 11 | 33859.5 | 28500 | 118.8%
[29 empty] | 2019 | October | 22 | 12 | 35777.5 | 28500 | 125.5%
[29 empty] | 2019 | October | 22 | 13 | 34160.5 | 28500 | 119.9%
[29 empty] | 2019 | October | 22 | 14 | 27423 | 28500 | 96.22%
[29 empty] | 2019 | October | 22 | 15 | 17265.5 | 28500 | 60.58%
[29 empty] | 2019 | October | 22 | 16 | 4610 | 28500 | 16.18%
[29 empty] | 2019 | October | 22 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 22 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 22 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 22 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 22 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 22 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 22 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 23 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 23 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 23 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 23 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 23 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 23 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 23 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 23 | 7 | 661.5 | 28500 | 2.321%
[29 empty] | 2019 | October | 23 | 8 | 5012.5 | 28500 | 17.59%
[29 empty] | 2019 | October | 23 | 9 | 2944.5 | 28500 | 10.33%
[29 empty] | 2019 | October | 23 | 10 | 4527.5 | 28500 | 15.89%
[29 empty] | 2019 | October | 23 | 11 | 12032.5 | 28500 | 42.22%
[29 empty] | 2019 | October | 23 | 12 | 18275 | 28500 | 64.12%
[29 empty] | 2019 | October | 23 | 13 | 10426.5 | 28500 | 36.58%
[29 empty] | 2019 | October | 23 | 14 | 1785 | 28500 | 6.263%
[29 empty] | 2019 | October | 23 | 15 | 1643.5 | 28500 | 5.767%
[29 empty] | 2019 | October | 23 | 16 | 139.5 | 28500 | 0.4895%
[29 empty] | 2019 | October | 23 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 23 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 23 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 23 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 23 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 23 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 23 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 24 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 24 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 24 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 24 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 24 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 24 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 24 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 24 | 7 | 141.5 | 28500 | 0.4965%
[29 empty] | 2019 | October | 24 | 8 | 662.5 | 28500 | 2.325%
[29 empty] | 2019 | October | 24 | 9 | 1373 | 28500 | 4.818%
[29 empty] | 2019 | October | 24 | 10 | 1127.5 | 28500 | 3.956%
[29 empty] | 2019 | October | 24 | 11 | 1126.5 | 28500 | 3.953%
[29 empty] | 2019 | October | 24 | 12 | 2172 | 28500 | 7.621%
[29 empty] | 2019 | October | 24 | 13 | 1590 | 28500 | 5.579%
[29 empty] | 2019 | October | 24 | 14 | 17768 | 28500 | 62.34%
[29 empty] | 2019 | October | 24 | 15 | 3215 | 28500 | 11.28%
[29 empty] | 2019 | October | 24 | 16 | 1171 | 28500 | 4.109%
[29 empty] | 2019 | October | 24 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 24 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 24 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 24 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 24 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 24 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 24 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 25 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 25 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 25 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 25 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 25 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 25 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 25 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 25 | 7 | 119 | 28500 | 0.4175%
[29 empty] | 2019 | October | 25 | 8 | 1387 | 28500 | 4.867%
[29 empty] | 2019 | October | 25 | 9 | 2025 | 28500 | 7.105%
[29 empty] | 2019 | October | 25 | 10 | 2193 | 28500 | 7.695%
[29 empty] | 2019 | October | 25 | 11 | 3655 | 28500 | 12.82%
[29 empty] | 2019 | October | 25 | 12 | 3047 | 28500 | 10.69%
[29 empty] | 2019 | October | 25 | 13 | 4494.5 | 28500 | 15.77%
[29 empty] | 2019 | October | 25 | 14 | 3187.5 | 28500 | 11.18%
[29 empty] | 2019 | October | 25 | 15 | 4856 | 28500 | 17.04%
[29 empty] | 2019 | October | 25 | 16 | 238 | 28500 | 0.8351%
[29 empty] | 2019 | October | 25 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 25 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 25 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 25 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 25 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 25 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 25 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 26 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 26 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 26 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 26 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 26 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 26 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 26 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 26 | 7 | 49 | 28500 | 0.1719%
[29 empty] | 2019 | October | 26 | 8 | 495.5 | 28500 | 1.739%
[29 empty] | 2019 | October | 26 | 9 | 3921 | 28500 | 13.76%
[29 empty] | 2019 | October | 26 | 10 | 679.5 | 28500 | 2.384%
[29 empty] | 2019 | October | 26 | 11 | 5002.5 | 28500 | 17.55%
[29 empty] | 2019 | October | 26 | 12 | 2394 | 28500 | 8.4%
[29 empty] | 2019 | October | 26 | 13 | 2359.5 | 28500 | 8.279%
[29 empty] | 2019 | October | 26 | 14 | 2108 | 28500 | 7.396%
[29 empty] | 2019 | October | 26 | 15 | 2108 | 28500 | 7.396%
[29 empty] | 2019 | October | 26 | 16 | 473.5 | 28500 | 1.661%
[29 empty] | 2019 | October | 26 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 26 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 26 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 26 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 26 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 26 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 26 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 27 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 27 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 27 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 27 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 27 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 27 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 27 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 27 | 7 | 406 | 28500 | 1.425%
[29 empty] | 2019 | October | 27 | 8 | 7069 | 28500 | 24.8%
[29 empty] | 2019 | October | 27 | 9 | 18223 | 28500 | 63.94%
[29 empty] | 2019 | October | 27 | 10 | 25221 | 28500 | 88.49%
[29 empty] | 2019 | October | 27 | 11 | 34578.5 | 28500 | 121.3%
[29 empty] | 2019 | October | 27 | 12 | 37542 | 28500 | 131.7%
[29 empty] | 2019 | October | 27 | 13 | 32580 | 28500 | 114.3%
[29 empty] | 2019 | October | 27 | 14 | 18432.5 | 28500 | 64.68%
[29 empty] | 2019 | October | 27 | 15 | 17244.5 | 28500 | 60.51%
[29 empty] | 2019 | October | 27 | 16 | 1777.5 | 28500 | 6.237%
[29 empty] | 2019 | October | 27 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 27 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 27 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 27 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 27 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 27 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 27 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 28 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 28 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 28 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 28 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 28 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 28 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 28 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 28 | 7 | 647.5 | 28500 | 2.272%
[29 empty] | 2019 | October | 28 | 8 | 11652.5 | 28500 | 40.89%
[29 empty] | 2019 | October | 28 | 9 | 24233 | 28500 | 85.03%
[29 empty] | 2019 | October | 28 | 10 | 29777.5 | 28500 | 104.5%
[29 empty] | 2019 | October | 28 | 11 | 33135 | 28500 | 116.3%
[29 empty] | 2019 | October | 28 | 12 | 27372 | 28500 | 96.04%
[29 empty] | 2019 | October | 28 | 13 | 13353.5 | 28500 | 46.85%
[29 empty] | 2019 | October | 28 | 14 | 6827 | 28500 | 23.95%
[29 empty] | 2019 | October | 28 | 15 | 7198 | 28500 | 25.26%
[29 empty] | 2019 | October | 28 | 16 | 672 | 28500 | 2.358%
[29 empty] | 2019 | October | 28 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 28 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 28 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 28 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 28 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 28 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 28 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 29 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 29 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 29 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 29 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 29 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 29 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 29 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 29 | 7 | 14.5 | 28500 | 0.05088%
[29 empty] | 2019 | October | 29 | 8 | 4152 | 28500 | 14.57%
[29 empty] | 2019 | October | 29 | 9 | 1729.5 | 28500 | 6.068%
[29 empty] | 2019 | October | 29 | 10 | 6246.5 | 28500 | 21.92%
[29 empty] | 2019 | October | 29 | 11 | 9245.5 | 28500 | 32.44%
[29 empty] | 2019 | October | 29 | 12 | 5240.5 | 28500 | 18.39%
[29 empty] | 2019 | October | 29 | 13 | 7421 | 28500 | 26.04%
[29 empty] | 2019 | October | 29 | 14 | 1453.5 | 28500 | 5.1%
[29 empty] | 2019 | October | 29 | 15 | 2869.5 | 28500 | 10.07%
[29 empty] | 2019 | October | 29 | 16 | 914.5 | 28500 | 3.209%
[29 empty] | 2019 | October | 29 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 29 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 29 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 29 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 29 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 29 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 29 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 30 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 30 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 30 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 30 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 30 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 30 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 30 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 30 | 7 | 837.5 | 28500 | 2.939%
[29 empty] | 2019 | October | 30 | 8 | 12468.5 | 28500 | 43.75%
[29 empty] | 2019 | October | 30 | 9 | 21256.5 | 28500 | 74.58%
[29 empty] | 2019 | October | 30 | 10 | 28020 | 28500 | 98.32%
[29 empty] | 2019 | October | 30 | 11 | 13778 | 28500 | 48.34%
[29 empty] | 2019 | October | 30 | 12 | 37386 | 28500 | 131.2%
[29 empty] | 2019 | October | 30 | 13 | 21255 | 28500 | 74.58%
[29 empty] | 2019 | October | 30 | 14 | 6550.5 | 28500 | 22.98%
[29 empty] | 2019 | October | 30 | 15 | 5658.5 | 28500 | 19.85%
[29 empty] | 2019 | October | 30 | 16 | 2153.5 | 28500 | 7.556%
[29 empty] | 2019 | October | 30 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 30 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 30 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 30 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 30 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 30 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 30 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 31 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 31 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 31 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 31 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 31 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 31 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 31 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 31 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 31 | 8 | 8335 | 28500 | 29.25%
[29 empty] | 2019 | October | 31 | 9 | 23879 | 28500 | 83.79%
[29 empty] | 2019 | October | 31 | 10 | 23888 | 28500 | 83.82%
[29 empty] | 2019 | October | 31 | 11 | 30450 | 28500 | 106.8%
[29 empty] | 2019 | October | 31 | 12 | 30199 | 28500 | 106%
[29 empty] | 2019 | October | 31 | 13 | 22874 | 28500 | 80.26%
[29 empty] | 2019 | October | 31 | 14 | 19095.5 | 28500 | 67%
[29 empty] | 2019 | October | 31 | 15 | 13266.5 | 28500 | 46.55%
[29 empty] | 2019 | October | 31 | 16 | 1147.5 | 28500 | 4.026%
[29 empty] | 2019 | October | 31 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 31 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 31 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 31 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 31 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 31 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | October | 31 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 1 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 1 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 1 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 1 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 1 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 1 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 1 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 1 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 1 | 8 | 661 | 28500 | 2.319%
[29 empty] | 2019 | November | 1 | 9 | 6755 | 28500 | 23.7%
[29 empty] | 2019 | November | 1 | 10 | 5744 | 28500 | 20.15%
[29 empty] | 2019 | November | 1 | 11 | 4553.5 | 28500 | 15.98%
[29 empty] | 2019 | November | 1 | 12 | 4960.5 | 28500 | 17.41%
[29 empty] | 2019 | November | 1 | 13 | 1740.5 | 28500 | 6.107%
[29 empty] | 2019 | November | 1 | 14 | 2181 | 28500 | 7.653%
[29 empty] | 2019 | November | 1 | 15 | 2799 | 28500 | 9.821%
[29 empty] | 2019 | November | 1 | 16 | 70.5 | 28500 | 0.2474%
[29 empty] | 2019 | November | 1 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 1 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 1 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 1 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 1 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 1 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 1 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 2 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 2 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 2 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 2 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 2 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 2 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 2 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 2 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 2 | 8 | 1004.5 | 28500 | 3.525%
[29 empty] | 2019 | November | 2 | 9 | 832.5 | 28500 | 2.921%
[29 empty] | 2019 | November | 2 | 10 | 637 | 28500 | 2.235%
[29 empty] | 2019 | November | 2 | 11 | 6465 | 28500 | 22.68%
[29 empty] | 2019 | November | 2 | 12 | 2300 | 28500 | 8.07%
[29 empty] | 2019 | November | 2 | 13 | 8295.5 | 28500 | 29.11%
[29 empty] | 2019 | November | 2 | 14 | 4182 | 28500 | 14.67%
[29 empty] | 2019 | November | 2 | 15 | 2864 | 28500 | 10.05%
[29 empty] | 2019 | November | 2 | 16 | 50.5 | 28500 | 0.1772%
[29 empty] | 2019 | November | 2 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 2 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 2 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 2 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 2 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 2 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 2 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 3 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 3 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 3 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 3 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 3 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 3 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 3 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 3 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 3 | 8 | 5993.5 | 28500 | 21.03%
[29 empty] | 2019 | November | 3 | 9 | 23016.5 | 28500 | 80.76%
[29 empty] | 2019 | November | 3 | 10 | 28587 | 28500 | 100.3%
[29 empty] | 2019 | November | 3 | 11 | 34497 | 28500 | 121%
[29 empty] | 2019 | November | 3 | 12 | 32991 | 28500 | 115.8%
[29 empty] | 2019 | November | 3 | 13 | 5728 | 28500 | 20.1%
[29 empty] | 2019 | November | 3 | 14 | 5446.5 | 28500 | 19.11%
[29 empty] | 2019 | November | 3 | 15 | 3008.5 | 28500 | 10.56%
[29 empty] | 2019 | November | 3 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 3 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 3 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 3 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 3 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 3 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 3 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 3 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 4 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 4 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 4 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 4 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 4 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 4 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 4 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 4 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 4 | 8 | 7244.5 | 28500 | 25.42%
[29 empty] | 2019 | November | 4 | 9 | 19472 | 28500 | 68.32%
[29 empty] | 2019 | November | 4 | 10 | 23093.5 | 28500 | 81.03%
[29 empty] | 2019 | November | 4 | 11 | 4521.5 | 28500 | 15.86%
[29 empty] | 2019 | November | 4 | 12 | 3196 | 28500 | 11.21%
[29 empty] | 2019 | November | 4 | 13 | 19367 | 28500 | 67.95%
[29 empty] | 2019 | November | 4 | 14 | 20305 | 28500 | 71.25%
[29 empty] | 2019 | November | 4 | 15 | 4550.5 | 28500 | 15.97%
[29 empty] | 2019 | November | 4 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 4 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 4 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 4 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 4 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 4 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 4 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 4 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 5 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 5 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 5 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 5 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 5 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 5 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 5 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 5 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 5 | 8 | 2677.5 | 28500 | 9.395%
[29 empty] | 2019 | November | 5 | 9 | 5014.5 | 28500 | 17.59%
[29 empty] | 2019 | November | 5 | 10 | 6918.5 | 28500 | 24.28%
[29 empty] | 2019 | November | 5 | 11 | 4530 | 28500 | 15.89%
[29 empty] | 2019 | November | 5 | 12 | 14867 | 28500 | 52.16%
[29 empty] | 2019 | November | 5 | 13 | 22464 | 28500 | 78.82%
[29 empty] | 2019 | November | 5 | 14 | 17807.5 | 28500 | 62.48%
[29 empty] | 2019 | November | 5 | 15 | 11461 | 28500 | 40.21%
[29 empty] | 2019 | November | 5 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 5 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 5 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 5 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 5 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 5 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 5 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 5 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 6 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 6 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 6 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 6 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 6 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 6 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 6 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 6 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 6 | 8 | 8044.5 | 28500 | 28.23%
[29 empty] | 2019 | November | 6 | 9 | 8476.5 | 28500 | 29.74%
[29 empty] | 2019 | November | 6 | 10 | 16066 | 28500 | 56.37%
[29 empty] | 2019 | November | 6 | 11 | 33264.5 | 28500 | 116.7%
[29 empty] | 2019 | November | 6 | 12 | 33053.5 | 28500 | 116%
[29 empty] | 2019 | November | 6 | 13 | 16690 | 28500 | 58.56%
[29 empty] | 2019 | November | 6 | 14 | 5817.5 | 28500 | 20.41%
[29 empty] | 2019 | November | 6 | 15 | 2297.5 | 28500 | 8.061%
[29 empty] | 2019 | November | 6 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 6 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 6 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 6 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 6 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 6 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 6 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 6 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 7 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 7 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 7 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 7 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 7 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 7 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 7 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 7 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 7 | 8 | 4940.5 | 28500 | 17.34%
[29 empty] | 2019 | November | 7 | 9 | 7332 | 28500 | 25.73%
[29 empty] | 2019 | November | 7 | 10 | 29020.5 | 28500 | 101.8%
[29 empty] | 2019 | November | 7 | 11 | 32521.5 | 28500 | 114.1%
[29 empty] | 2019 | November | 7 | 12 | 34081 | 28500 | 119.6%
[29 empty] | 2019 | November | 7 | 13 | 30520.5 | 28500 | 107.1%
[29 empty] | 2019 | November | 7 | 14 | 20370 | 28500 | 71.47%
[29 empty] | 2019 | November | 7 | 15 | 10588 | 28500 | 37.15%
[29 empty] | 2019 | November | 7 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 7 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 7 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 7 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 7 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 7 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 7 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 7 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 8 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 8 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 8 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 8 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 8 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 8 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 8 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 8 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 8 | 8 | 7276.5 | 28500 | 25.53%
[29 empty] | 2019 | November | 8 | 9 | 26093.5 | 28500 | 91.56%
[29 empty] | 2019 | November | 8 | 10 | 32533 | 28500 | 114.2%
[29 empty] | 2019 | November | 8 | 11 | 21479 | 28500 | 75.36%
[29 empty] | 2019 | November | 8 | 12 | 13803.5 | 28500 | 48.43%
[29 empty] | 2019 | November | 8 | 13 | 1360.5 | 28500 | 4.774%
[29 empty] | 2019 | November | 8 | 14 | 1615 | 28500 | 5.667%
[29 empty] | 2019 | November | 8 | 15 | 4841 | 28500 | 16.99%
[29 empty] | 2019 | November | 8 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 8 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 8 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 8 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 8 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 8 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 8 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 8 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 9 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 9 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 9 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 9 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 9 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 9 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 9 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 9 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 9 | 8 | 5823 | 28500 | 20.43%
[29 empty] | 2019 | November | 9 | 9 | 20191 | 28500 | 70.85%
[29 empty] | 2019 | November | 9 | 10 | 20898.5 | 28500 | 73.33%
[29 empty] | 2019 | November | 9 | 11 | 29584 | 28500 | 103.8%
[29 empty] | 2019 | November | 9 | 12 | 13010 | 28500 | 45.65%
[29 empty] | 2019 | November | 9 | 13 | 14430 | 28500 | 50.63%
[29 empty] | 2019 | November | 9 | 14 | 2628.5 | 28500 | 9.223%
[29 empty] | 2019 | November | 9 | 15 | 1331.5 | 28500 | 4.672%
[29 empty] | 2019 | November | 9 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 9 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 9 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 9 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 9 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 9 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 9 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 9 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 10 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 10 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 10 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 10 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 10 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 10 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 10 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 10 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 10 | 8 | 5662 | 28500 | 19.87%
[29 empty] | 2019 | November | 10 | 9 | 19658 | 28500 | 68.98%
[29 empty] | 2019 | November | 10 | 10 | 29804 | 28500 | 104.6%
[29 empty] | 2019 | November | 10 | 11 | 34495.5 | 28500 | 121%
[29 empty] | 2019 | November | 10 | 12 | 14921.5 | 28500 | 52.36%
[29 empty] | 2019 | November | 10 | 13 | 15619 | 28500 | 54.8%
[29 empty] | 2019 | November | 10 | 14 | 14468.5 | 28500 | 50.77%
[29 empty] | 2019 | November | 10 | 15 | 9927.5 | 28500 | 34.83%
[29 empty] | 2019 | November | 10 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 10 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 10 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 10 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 10 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 10 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 10 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 10 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 11 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 11 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 11 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 11 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 11 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 11 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 11 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 11 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 11 | 8 | 2997.5 | 28500 | 10.52%
[29 empty] | 2019 | November | 11 | 9 | 20467.5 | 28500 | 71.82%
[29 empty] | 2019 | November | 11 | 10 | 25136 | 28500 | 88.2%
[29 empty] | 2019 | November | 11 | 11 | 13767.5 | 28500 | 48.31%
[29 empty] | 2019 | November | 11 | 12 | 2725.5 | 28500 | 9.563%
[29 empty] | 2019 | November | 11 | 13 | 26446.5 | 28500 | 92.79%
[29 empty] | 2019 | November | 11 | 14 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 11 | 15 | 5945 | 28500 | 20.86%
[29 empty] | 2019 | November | 11 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 11 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 11 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 11 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 11 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 11 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 11 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 11 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 12 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 12 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 12 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 12 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 12 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 12 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 12 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 12 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 12 | 8 | 6612.5 | 28500 | 23.2%
[29 empty] | 2019 | November | 12 | 9 | 20565.5 | 28500 | 72.16%
[29 empty] | 2019 | November | 12 | 10 | 29251 | 28500 | 102.6%
[29 empty] | 2019 | November | 12 | 11 | 35120 | 28500 | 123.2%
[29 empty] | 2019 | November | 12 | 12 | 21833 | 28500 | 76.61%
[29 empty] | 2019 | November | 12 | 13 | 1745.5 | 28500 | 6.125%
[29 empty] | 2019 | November | 12 | 14 | 11476 | 28500 | 40.27%
[29 empty] | 2019 | November | 12 | 15 | 6276 | 28500 | 22.02%
[29 empty] | 2019 | November | 12 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 12 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 12 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 12 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 12 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 12 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 12 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 12 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 13 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 13 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 13 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 13 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 13 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 13 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 13 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 13 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 13 | 8 | 9073.5 | 28500 | 31.84%
[29 empty] | 2019 | November | 13 | 9 | 21922.5 | 28500 | 76.92%
[29 empty] | 2019 | November | 13 | 10 | 27164.5 | 28500 | 95.31%
[29 empty] | 2019 | November | 13 | 11 | 32656 | 28500 | 114.6%
[29 empty] | 2019 | November | 13 | 12 | 31789.5 | 28500 | 111.5%
[29 empty] | 2019 | November | 13 | 13 | 20882 | 28500 | 73.27%
[29 empty] | 2019 | November | 13 | 14 | 22103.5 | 28500 | 77.56%
[29 empty] | 2019 | November | 13 | 15 | 2799.5 | 28500 | 9.823%
[29 empty] | 2019 | November | 13 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 13 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 13 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 13 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 13 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 13 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 13 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 13 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 14 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 14 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 14 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 14 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 14 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 14 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 14 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 14 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 14 | 8 | 4443 | 28500 | 15.59%
[29 empty] | 2019 | November | 14 | 9 | 19609 | 28500 | 68.8%
[29 empty] | 2019 | November | 14 | 10 | 28296 | 28500 | 99.28%
[29 empty] | 2019 | November | 14 | 11 | 30486 | 28500 | 107%
[29 empty] | 2019 | November | 14 | 12 | 33934 | 28500 | 119.1%
[29 empty] | 2019 | November | 14 | 13 | 28573 | 28500 | 100.3%
[29 empty] | 2019 | November | 14 | 14 | 22516.5 | 28500 | 79.01%
[29 empty] | 2019 | November | 14 | 15 | 613.5 | 28500 | 2.153%
[29 empty] | 2019 | November | 14 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 14 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 14 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 14 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 14 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 14 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 14 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 14 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 15 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 15 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 15 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 15 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 15 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 15 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 15 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 15 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 15 | 8 | 402 | 28500 | 1.411%
[29 empty] | 2019 | November | 15 | 9 | 1423 | 28500 | 4.993%
[29 empty] | 2019 | November | 15 | 10 | 1128.5 | 28500 | 3.96%
[29 empty] | 2019 | November | 15 | 11 | 6071.5 | 28500 | 21.3%
[29 empty] | 2019 | November | 15 | 12 | 6785.5 | 28500 | 23.81%
[29 empty] | 2019 | November | 15 | 13 | 1775 | 28500 | 6.228%
[29 empty] | 2019 | November | 15 | 14 | 1999 | 28500 | 7.014%
[29 empty] | 2019 | November | 15 | 15 | 614 | 28500 | 2.154%
[29 empty] | 2019 | November | 15 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 15 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 15 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 15 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 15 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 15 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 15 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 15 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 16 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 16 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 16 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 16 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 16 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 16 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 16 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 16 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 16 | 8 | 3220 | 28500 | 11.3%
[29 empty] | 2019 | November | 16 | 9 | 6211 | 28500 | 21.79%
[29 empty] | 2019 | November | 16 | 10 | 9511.5 | 28500 | 33.37%
[29 empty] | 2019 | November | 16 | 11 | 12387 | 28500 | 43.46%
[29 empty] | 2019 | November | 16 | 12 | 13133 | 28500 | 46.08%
[29 empty] | 2019 | November | 16 | 13 | 2332 | 28500 | 8.182%
[29 empty] | 2019 | November | 16 | 14 | 612.5 | 28500 | 2.149%
[29 empty] | 2019 | November | 16 | 15 | 456 | 28500 | 1.6%
[29 empty] | 2019 | November | 16 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 16 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 16 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 16 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 16 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 16 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 16 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 16 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 17 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 17 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 17 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 17 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 17 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 17 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 17 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 17 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 17 | 8 | 1462 | 28500 | 5.13%
[29 empty] | 2019 | November | 17 | 9 | 5555.5 | 28500 | 19.49%
[29 empty] | 2019 | November | 17 | 10 | 22552.5 | 28500 | 79.13%
[29 empty] | 2019 | November | 17 | 11 | 26706.5 | 28500 | 93.71%
[29 empty] | 2019 | November | 17 | 12 | 23989 | 28500 | 84.17%
[29 empty] | 2019 | November | 17 | 13 | 5521.5 | 28500 | 19.37%
[29 empty] | 2019 | November | 17 | 14 | 5001 | 28500 | 17.55%
[29 empty] | 2019 | November | 17 | 15 | 1865.5 | 28500 | 6.546%
[29 empty] | 2019 | November | 17 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 17 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 17 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 17 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 17 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 17 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 17 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 17 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 18 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 18 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 18 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 18 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 18 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 18 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 18 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 18 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 18 | 8 | 3765.5 | 28500 | 13.21%
[29 empty] | 2019 | November | 18 | 9 | 1995.5 | 28500 | 7.002%
[29 empty] | 2019 | November | 18 | 10 | 27036 | 28500 | 94.86%
[29 empty] | 2019 | November | 18 | 11 | 15776 | 28500 | 55.35%
[29 empty] | 2019 | November | 18 | 12 | 24588 | 28500 | 86.27%
[29 empty] | 2019 | November | 18 | 13 | 2113.5 | 28500 | 7.416%
[29 empty] | 2019 | November | 18 | 14 | 4180.5 | 28500 | 14.67%
[29 empty] | 2019 | November | 18 | 15 | 1318.5 | 28500 | 4.626%
[29 empty] | 2019 | November | 18 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 18 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 18 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 18 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 18 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 18 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 18 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 18 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 19 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 19 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 19 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 19 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 19 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 19 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 19 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 19 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 19 | 8 | 4091 | 28500 | 14.35%
[29 empty] | 2019 | November | 19 | 9 | 8221.5 | 28500 | 28.85%
[29 empty] | 2019 | November | 19 | 10 | 2557 | 28500 | 8.972%
[29 empty] | 2019 | November | 19 | 11 | 5030 | 28500 | 17.65%
[29 empty] | 2019 | November | 19 | 12 | 10134.5 | 28500 | 35.56%
[29 empty] | 2019 | November | 19 | 13 | 8367 | 28500 | 29.36%
[29 empty] | 2019 | November | 19 | 14 | 11155 | 28500 | 39.14%
[29 empty] | 2019 | November | 19 | 15 | 2988 | 28500 | 10.48%
[29 empty] | 2019 | November | 19 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 19 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 19 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 19 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 19 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 19 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 19 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 19 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 20 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 20 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 20 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 20 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 20 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 20 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 20 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 20 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 20 | 8 | 3186.5 | 28500 | 11.18%
[29 empty] | 2019 | November | 20 | 9 | 5332 | 28500 | 18.71%
[29 empty] | 2019 | November | 20 | 10 | 17454.5 | 28500 | 61.24%
[29 empty] | 2019 | November | 20 | 11 | 21139.5 | 28500 | 74.17%
[29 empty] | 2019 | November | 20 | 12 | 22372.5 | 28500 | 78.5%
[29 empty] | 2019 | November | 20 | 13 | 14422 | 28500 | 50.6%
[29 empty] | 2019 | November | 20 | 14 | 14737 | 28500 | 51.71%
[29 empty] | 2019 | November | 20 | 15 | 4186.5 | 28500 | 14.69%
[29 empty] | 2019 | November | 20 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 20 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 20 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 20 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 20 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 20 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 20 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 20 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 21 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 21 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 21 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 21 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 21 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 21 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 21 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 21 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 21 | 8 | 1334.5 | 28500 | 4.682%
[29 empty] | 2019 | November | 21 | 9 | 2352 | 28500 | 8.253%
[29 empty] | 2019 | November | 21 | 10 | 4270.5 | 28500 | 14.98%
[29 empty] | 2019 | November | 21 | 11 | 2215 | 28500 | 7.772%
[29 empty] | 2019 | November | 21 | 12 | 1313.5 | 28500 | 4.609%
[29 empty] | 2019 | November | 21 | 13 | 1025.5 | 28500 | 3.598%
[29 empty] | 2019 | November | 21 | 14 | 553.5 | 28500 | 1.942%
[29 empty] | 2019 | November | 21 | 15 | 1176.5 | 28500 | 4.128%
[29 empty] | 2019 | November | 21 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 21 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 21 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 21 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 21 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 21 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 21 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 21 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 22 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 22 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 22 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 22 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 22 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 22 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 22 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 22 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 22 | 8 | 1879.5 | 28500 | 6.595%
[29 empty] | 2019 | November | 22 | 9 | 13565.5 | 28500 | 47.6%
[29 empty] | 2019 | November | 22 | 10 | 4771 | 28500 | 16.74%
[29 empty] | 2019 | November | 22 | 11 | 1435 | 28500 | 5.035%
[29 empty] | 2019 | November | 22 | 12 | 1077.5 | 28500 | 3.781%
[29 empty] | 2019 | November | 22 | 13 | 7566.5 | 28500 | 26.55%
[29 empty] | 2019 | November | 22 | 14 | 1111.5 | 28500 | 3.9%
[29 empty] | 2019 | November | 22 | 15 | 1124.5 | 28500 | 3.946%
[29 empty] | 2019 | November | 22 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 22 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 22 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 22 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 22 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 22 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 22 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 22 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 23 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 23 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 23 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 23 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 23 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 23 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 23 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 23 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 23 | 8 | 542 | 28500 | 1.902%
[29 empty] | 2019 | November | 23 | 9 | 610 | 28500 | 2.14%
[29 empty] | 2019 | November | 23 | 10 | 4667.5 | 28500 | 16.38%
[29 empty] | 2019 | November | 23 | 11 | 2414.5 | 28500 | 8.472%
[29 empty] | 2019 | November | 23 | 12 | 5096.5 | 28500 | 17.88%
[29 empty] | 2019 | November | 23 | 13 | 2898 | 28500 | 10.17%
[29 empty] | 2019 | November | 23 | 14 | 1244 | 28500 | 4.365%
[29 empty] | 2019 | November | 23 | 15 | 52 | 28500 | 0.1825%
[29 empty] | 2019 | November | 23 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 23 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 23 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 23 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 23 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 23 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 23 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 23 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 24 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 24 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 24 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 24 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 24 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 24 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 24 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 24 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 24 | 8 | 849.5 | 28500 | 2.981%
[29 empty] | 2019 | November | 24 | 9 | 302 | 28500 | 1.06%
[29 empty] | 2019 | November | 24 | 10 | 799 | 28500 | 2.804%
[29 empty] | 2019 | November | 24 | 11 | 831 | 28500 | 2.916%
[29 empty] | 2019 | November | 24 | 12 | 1708 | 28500 | 5.993%
[29 empty] | 2019 | November | 24 | 13 | 13882.5 | 28500 | 48.71%
[29 empty] | 2019 | November | 24 | 14 | 11281 | 28500 | 39.58%
[29 empty] | 2019 | November | 24 | 15 | 2872 | 28500 | 10.08%
[29 empty] | 2019 | November | 24 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 24 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 24 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 24 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 24 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 24 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 24 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 24 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 25 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 25 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 25 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 25 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 25 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 25 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 25 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 25 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 25 | 8 | 841 | 28500 | 2.951%
[29 empty] | 2019 | November | 25 | 9 | 480 | 28500 | 1.684%
[29 empty] | 2019 | November | 25 | 10 | 6033.5 | 28500 | 21.17%
[29 empty] | 2019 | November | 25 | 11 | 2611 | 28500 | 9.161%
[29 empty] | 2019 | November | 25 | 12 | 1711.5 | 28500 | 6.005%
[29 empty] | 2019 | November | 25 | 13 | 2602.5 | 28500 | 9.132%
[29 empty] | 2019 | November | 25 | 14 | 167 | 28500 | 0.586%
[29 empty] | 2019 | November | 25 | 15 | 1042.5 | 28500 | 3.658%
[29 empty] | 2019 | November | 25 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 25 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 25 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 25 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 25 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 25 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 25 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 25 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 26 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 26 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 26 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 26 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 26 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 26 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 26 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 26 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 26 | 8 | 219.5 | 28500 | 0.7702%
[29 empty] | 2019 | November | 26 | 9 | 2277.5 | 28500 | 7.991%
[29 empty] | 2019 | November | 26 | 10 | 1674.5 | 28500 | 5.875%
[29 empty] | 2019 | November | 26 | 11 | 3930 | 28500 | 13.79%
[29 empty] | 2019 | November | 26 | 12 | 2781.5 | 28500 | 9.76%
[29 empty] | 2019 | November | 26 | 13 | 4185.5 | 28500 | 14.69%
[29 empty] | 2019 | November | 26 | 14 | 15617 | 28500 | 54.8%
[29 empty] | 2019 | November | 26 | 15 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 26 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 26 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 26 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 26 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 26 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 26 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 26 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 26 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 27 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 27 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 27 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 27 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 27 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 27 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 27 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 27 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 27 | 8 | 495 | 28500 | 1.737%
[29 empty] | 2019 | November | 27 | 9 | 2731 | 28500 | 9.582%
[29 empty] | 2019 | November | 27 | 10 | 18146 | 28500 | 63.67%
[29 empty] | 2019 | November | 27 | 11 | 14538 | 28500 | 51.01%
[29 empty] | 2019 | November | 27 | 12 | 603.5 | 28500 | 2.118%
[29 empty] | 2019 | November | 27 | 13 | 4714 | 28500 | 16.54%
[29 empty] | 2019 | November | 27 | 14 | 1527.5 | 28500 | 5.36%
[29 empty] | 2019 | November | 27 | 15 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 27 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 27 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 27 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 27 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 27 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 27 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 27 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 27 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 28 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 28 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 28 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 28 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 28 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 28 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 28 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 28 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 28 | 8 | 448 | 28500 | 1.572%
[29 empty] | 2019 | November | 28 | 9 | 2728.5 | 28500 | 9.574%
[29 empty] | 2019 | November | 28 | 10 | 3165 | 28500 | 11.11%
[29 empty] | 2019 | November | 28 | 11 | 1221.5 | 28500 | 4.286%
[29 empty] | 2019 | November | 28 | 12 | 452 | 28500 | 1.586%
[29 empty] | 2019 | November | 28 | 13 | 1182.5 | 28500 | 4.149%
[29 empty] | 2019 | November | 28 | 14 | 939.5 | 28500 | 3.296%
[29 empty] | 2019 | November | 28 | 15 | 3541.5 | 28500 | 12.43%
[29 empty] | 2019 | November | 28 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 28 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 28 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 28 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 28 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 28 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 28 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 28 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 29 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 29 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 29 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 29 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 29 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 29 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 29 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 29 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 29 | 8 | 1312.5 | 28500 | 4.605%
[29 empty] | 2019 | November | 29 | 9 | 15749 | 28500 | 55.26%
[29 empty] | 2019 | November | 29 | 10 | 25809.5 | 28500 | 90.56%
[29 empty] | 2019 | November | 29 | 11 | 32119 | 28500 | 112.7%
[29 empty] | 2019 | November | 29 | 12 | 31549.5 | 28500 | 110.7%
[29 empty] | 2019 | November | 29 | 13 | 27499 | 28500 | 96.49%
[29 empty] | 2019 | November | 29 | 14 | 22882.5 | 28500 | 80.29%
[29 empty] | 2019 | November | 29 | 15 | 7882.5 | 28500 | 27.66%
[29 empty] | 2019 | November | 29 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 29 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 29 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 29 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 29 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 29 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 29 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 29 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 30 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 30 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 30 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 30 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 30 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 30 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 30 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 30 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 30 | 8 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 30 | 9 | 4151.5 | 28500 | 14.57%
[29 empty] | 2019 | November | 30 | 10 | 9207.5 | 28500 | 32.31%
[29 empty] | 2019 | November | 30 | 11 | 14509 | 28500 | 50.91%
[29 empty] | 2019 | November | 30 | 12 | 15544.5 | 28500 | 54.54%
[29 empty] | 2019 | November | 30 | 13 | 11225.5 | 28500 | 39.39%
[29 empty] | 2019 | November | 30 | 14 | 23584.5 | 28500 | 82.75%
[29 empty] | 2019 | November | 30 | 15 | 4643.5 | 28500 | 16.29%
[29 empty] | 2019 | November | 30 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 30 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 30 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 30 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 30 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 30 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 30 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | November | 30 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 1 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 1 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 1 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 1 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 1 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 1 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 1 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 1 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 1 | 8 | 124 | 28500 | 0.4351%
[29 empty] | 2019 | December | 1 | 9 | 99.5 | 28500 | 0.3491%
[29 empty] | 2019 | December | 1 | 10 | 4610.5 | 28500 | 16.18%
[29 empty] | 2019 | December | 1 | 11 | 32788.5 | 28500 | 115%
[29 empty] | 2019 | December | 1 | 12 | 4563 | 28500 | 16.01%
[29 empty] | 2019 | December | 1 | 13 | 27326.5 | 28500 | 95.88%
[29 empty] | 2019 | December | 1 | 14 | 1089.5 | 28500 | 3.823%
[29 empty] | 2019 | December | 1 | 15 | 717 | 28500 | 2.516%
[29 empty] | 2019 | December | 1 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 1 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 1 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 1 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 1 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 1 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 1 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 1 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 2 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 2 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 2 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 2 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 2 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 2 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 2 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 2 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 2 | 8 | 1394.5 | 28500 | 4.893%
[29 empty] | 2019 | December | 2 | 9 | 13980.5 | 28500 | 49.05%
[29 empty] | 2019 | December | 2 | 10 | 25717.5 | 28500 | 90.24%
[29 empty] | 2019 | December | 2 | 11 | 30163 | 28500 | 105.8%
[29 empty] | 2019 | December | 2 | 12 | 31086.5 | 28500 | 109.1%
[29 empty] | 2019 | December | 2 | 13 | 27331.5 | 28500 | 95.9%
[29 empty] | 2019 | December | 2 | 14 | 20905 | 28500 | 73.35%
[29 empty] | 2019 | December | 2 | 15 | 6027 | 28500 | 21.15%
[29 empty] | 2019 | December | 2 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 2 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 2 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 2 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 2 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 2 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 2 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 2 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 3 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 3 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 3 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 3 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 3 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 3 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 3 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 3 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 3 | 8 | 35.5 | 28500 | 0.1246%
[29 empty] | 2019 | December | 3 | 9 | 6534.5 | 28500 | 22.93%
[29 empty] | 2019 | December | 3 | 10 | 22383.5 | 28500 | 78.54%
[29 empty] | 2019 | December | 3 | 11 | 27873 | 28500 | 97.8%
[29 empty] | 2019 | December | 3 | 12 | 29227 | 28500 | 102.6%
[29 empty] | 2019 | December | 3 | 13 | 25904.5 | 28500 | 90.89%
[29 empty] | 2019 | December | 3 | 14 | 19313.5 | 28500 | 67.77%
[29 empty] | 2019 | December | 3 | 15 | 6295.5 | 28500 | 22.09%
[29 empty] | 2019 | December | 3 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 3 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 3 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 3 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 3 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 3 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 3 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 3 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 4 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 4 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 4 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 4 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 4 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 4 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 4 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 4 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 4 | 8 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 4 | 9 | 13657.5 | 28500 | 47.92%
[29 empty] | 2019 | December | 4 | 10 | 24569.5 | 28500 | 86.21%
[29 empty] | 2019 | December | 4 | 11 | 29490 | 28500 | 103.5%
[29 empty] | 2019 | December | 4 | 12 | 30191.5 | 28500 | 105.9%
[29 empty] | 2019 | December | 4 | 13 | 26623 | 28500 | 93.41%
[29 empty] | 2019 | December | 4 | 14 | 20679.5 | 28500 | 72.56%
[29 empty] | 2019 | December | 4 | 15 | 7091 | 28500 | 24.88%
[29 empty] | 2019 | December | 4 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 4 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 4 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 4 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 4 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 4 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 4 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 4 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 5 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 5 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 5 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 5 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 5 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 5 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 5 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 5 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 5 | 8 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 5 | 9 | 4375 | 28500 | 15.35%
[29 empty] | 2019 | December | 5 | 10 | 5444.5 | 28500 | 19.1%
[29 empty] | 2019 | December | 5 | 11 | 5808.5 | 28500 | 20.38%
[29 empty] | 2019 | December | 5 | 12 | 13288 | 28500 | 46.62%
[29 empty] | 2019 | December | 5 | 13 | 8675 | 28500 | 30.44%
[29 empty] | 2019 | December | 5 | 14 | 1671 | 28500 | 5.863%
[29 empty] | 2019 | December | 5 | 15 | 667 | 28500 | 2.34%
[29 empty] | 2019 | December | 5 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 5 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 5 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 5 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 5 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 5 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 5 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 5 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 6 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 6 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 6 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 6 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 6 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 6 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 6 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 6 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 6 | 8 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 6 | 9 | 245 | 28500 | 0.8596%
[29 empty] | 2019 | December | 6 | 10 | 13021 | 28500 | 45.69%
[29 empty] | 2019 | December | 6 | 11 | 795 | 28500 | 2.789%
[29 empty] | 2019 | December | 6 | 12 | 1379 | 28500 | 4.839%
[29 empty] | 2019 | December | 6 | 13 | 893 | 28500 | 3.133%
[29 empty] | 2019 | December | 6 | 14 | 15423.5 | 28500 | 54.12%
[29 empty] | 2019 | December | 6 | 15 | 1332 | 28500 | 4.674%
[29 empty] | 2019 | December | 6 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 6 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 6 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 6 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 6 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 6 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 6 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 6 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 7 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 7 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 7 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 7 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 7 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 7 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 7 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 7 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 7 | 8 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 7 | 9 | 617 | 28500 | 2.165%
[29 empty] | 2019 | December | 7 | 10 | 2990 | 28500 | 10.49%
[29 empty] | 2019 | December | 7 | 11 | 3960 | 28500 | 13.89%
[29 empty] | 2019 | December | 7 | 12 | 9399 | 28500 | 32.98%
[29 empty] | 2019 | December | 7 | 13 | 12442 | 28500 | 43.66%
[29 empty] | 2019 | December | 7 | 14 | 15436.5 | 28500 | 54.16%
[29 empty] | 2019 | December | 7 | 15 | 634.5 | 28500 | 2.226%
[29 empty] | 2019 | December | 7 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 7 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 7 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 7 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 7 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 7 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 7 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 7 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 8 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 8 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 8 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 8 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 8 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 8 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 8 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 8 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 8 | 8 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 8 | 9 | 8747 | 28500 | 30.69%
[29 empty] | 2019 | December | 8 | 10 | 19874 | 28500 | 69.73%
[29 empty] | 2019 | December | 8 | 11 | 26475.5 | 28500 | 92.9%
[29 empty] | 2019 | December | 8 | 12 | 27596.5 | 28500 | 96.83%
[29 empty] | 2019 | December | 8 | 13 | 4295 | 28500 | 15.07%
[29 empty] | 2019 | December | 8 | 14 | 2572 | 28500 | 9.025%
[29 empty] | 2019 | December | 8 | 15 | 2441.5 | 28500 | 8.567%
[29 empty] | 2019 | December | 8 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 8 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 8 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 8 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 8 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 8 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 8 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 8 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 9 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 9 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 9 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 9 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 9 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 9 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 9 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 9 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 9 | 8 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 9 | 9 | 14367 | 28500 | 50.41%
[29 empty] | 2019 | December | 9 | 10 | 23858.5 | 28500 | 83.71%
[29 empty] | 2019 | December | 9 | 11 | 25870.5 | 28500 | 90.77%
[29 empty] | 2019 | December | 9 | 12 | 29052.5 | 28500 | 101.9%
[29 empty] | 2019 | December | 9 | 13 | 25208 | 28500 | 88.45%
[29 empty] | 2019 | December | 9 | 14 | 15534.5 | 28500 | 54.51%
[29 empty] | 2019 | December | 9 | 15 | 8087.5 | 28500 | 28.38%
[29 empty] | 2019 | December | 9 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 9 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 9 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 9 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 9 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 9 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 9 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 9 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 10 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 10 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 10 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 10 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 10 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 10 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 10 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 10 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 10 | 8 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 10 | 9 | 1877 | 28500 | 6.586%
[29 empty] | 2019 | December | 10 | 10 | 2053 | 28500 | 7.204%
[29 empty] | 2019 | December | 10 | 11 | 1692.5 | 28500 | 5.939%
[29 empty] | 2019 | December | 10 | 12 | 941.5 | 28500 | 3.304%
[29 empty] | 2019 | December | 10 | 13 | 1185 | 28500 | 4.158%
[29 empty] | 2019 | December | 10 | 14 | 1078 | 28500 | 3.782%
[29 empty] | 2019 | December | 10 | 15 | 52 | 28500 | 0.1825%
[29 empty] | 2019 | December | 10 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 10 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 10 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 10 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 10 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 10 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 10 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 10 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 11 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 11 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 11 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 11 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 11 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 11 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 11 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 11 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 11 | 8 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 11 | 9 | 18466 | 28500 | 64.79%
[29 empty] | 2019 | December | 11 | 10 | 25260.5 | 28500 | 88.63%
[29 empty] | 2019 | December | 11 | 11 | 28290 | 28500 | 99.26%
[29 empty] | 2019 | December | 11 | 12 | 25319 | 28500 | 88.84%
[29 empty] | 2019 | December | 11 | 13 | 28761 | 28500 | 100.9%
[29 empty] | 2019 | December | 11 | 14 | 20979 | 28500 | 73.61%
[29 empty] | 2019 | December | 11 | 15 | 97.5 | 28500 | 0.3421%
[29 empty] | 2019 | December | 11 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 11 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 11 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 11 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 11 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 11 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 11 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 11 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 12 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 12 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 12 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 12 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 12 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 12 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 12 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 12 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 12 | 8 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 12 | 9 | 623.5 | 28500 | 2.188%
[29 empty] | 2019 | December | 12 | 10 | 652 | 28500 | 2.288%
[29 empty] | 2019 | December | 12 | 11 | 5306.5 | 28500 | 18.62%
[29 empty] | 2019 | December | 12 | 12 | 9312 | 28500 | 32.67%
[29 empty] | 2019 | December | 12 | 13 | 748.5 | 28500 | 2.626%
[29 empty] | 2019 | December | 12 | 14 | 711.5 | 28500 | 2.496%
[29 empty] | 2019 | December | 12 | 15 | 1336 | 28500 | 4.688%
[29 empty] | 2019 | December | 12 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 12 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 12 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 12 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 12 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 12 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 12 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 12 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 13 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 13 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 13 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 13 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 13 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 13 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 13 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 13 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 13 | 8 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 13 | 9 | 5915.5 | 28500 | 20.76%
[29 empty] | 2019 | December | 13 | 10 | 5653.5 | 28500 | 19.84%
[29 empty] | 2019 | December | 13 | 11 | 3527.5 | 28500 | 12.38%
[29 empty] | 2019 | December | 13 | 12 | 22165.5 | 28500 | 77.77%
[29 empty] | 2019 | December | 13 | 13 | 6565.5 | 28500 | 23.04%
[29 empty] | 2019 | December | 13 | 14 | 2328 | 28500 | 8.168%
[29 empty] | 2019 | December | 13 | 15 | 526 | 28500 | 1.846%
[29 empty] | 2019 | December | 13 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 13 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 13 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 13 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 13 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 13 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 13 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 13 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 14 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 14 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 14 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 14 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 14 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 14 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 14 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 14 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 14 | 8 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 14 | 9 | 5449.5 | 28500 | 19.12%
[29 empty] | 2019 | December | 14 | 10 | 2895 | 28500 | 10.16%
[29 empty] | 2019 | December | 14 | 11 | 11286.5 | 28500 | 39.6%
[29 empty] | 2019 | December | 14 | 12 | 28799.5 | 28500 | 101.1%
[29 empty] | 2019 | December | 14 | 13 | 3760.5 | 28500 | 13.19%
[29 empty] | 2019 | December | 14 | 14 | 3718 | 28500 | 13.05%
[29 empty] | 2019 | December | 14 | 15 | 9021 | 28500 | 31.65%
[29 empty] | 2019 | December | 14 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 14 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 14 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 14 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 14 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 14 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 14 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 14 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 15 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 15 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 15 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 15 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 15 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 15 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 15 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 15 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 15 | 8 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 15 | 9 | 11923 | 28500 | 41.84%
[29 empty] | 2019 | December | 15 | 10 | 27103 | 28500 | 95.1%
[29 empty] | 2019 | December | 15 | 11 | 28936 | 28500 | 101.5%
[29 empty] | 2019 | December | 15 | 12 | 29854.5 | 28500 | 104.8%
[29 empty] | 2019 | December | 15 | 13 | 25755.5 | 28500 | 90.37%
[29 empty] | 2019 | December | 15 | 14 | 17489.5 | 28500 | 61.37%
[29 empty] | 2019 | December | 15 | 15 | 3944.5 | 28500 | 13.84%
[29 empty] | 2019 | December | 15 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 15 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 15 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 15 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 15 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 15 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 15 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 15 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 16 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 16 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 16 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 16 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 16 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 16 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 16 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 16 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 16 | 8 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 16 | 9 | 308 | 28500 | 1.081%
[29 empty] | 2019 | December | 16 | 10 | 12972.5 | 28500 | 45.52%
[29 empty] | 2019 | December | 16 | 11 | 13668.5 | 28500 | 47.96%
[29 empty] | 2019 | December | 16 | 12 | 7602 | 28500 | 26.67%
[29 empty] | 2019 | December | 16 | 13 | 5575.5 | 28500 | 19.56%
[29 empty] | 2019 | December | 16 | 14 | 4389.5 | 28500 | 15.4%
[29 empty] | 2019 | December | 16 | 15 | 170 | 28500 | 0.5965%
[29 empty] | 2019 | December | 16 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 16 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 16 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 16 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 16 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 16 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 16 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 16 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 17 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 17 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 17 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 17 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 17 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 17 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 17 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 17 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 17 | 8 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 17 | 9 | 4486.5 | 28500 | 15.74%
[29 empty] | 2019 | December | 17 | 10 | 3274 | 28500 | 11.49%
[29 empty] | 2019 | December | 17 | 11 | 3445.5 | 28500 | 12.09%
[29 empty] | 2019 | December | 17 | 12 | 11014 | 28500 | 38.65%
[29 empty] | 2019 | December | 17 | 13 | 4196 | 28500 | 14.72%
[29 empty] | 2019 | December | 17 | 14 | 1999 | 28500 | 7.014%
[29 empty] | 2019 | December | 17 | 15 | 627 | 28500 | 2.2%
[29 empty] | 2019 | December | 17 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 17 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 17 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 17 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 17 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 17 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 17 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 17 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 18 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 18 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 18 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 18 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 18 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 18 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 18 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 18 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 18 | 8 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 18 | 9 | 8451.5 | 28500 | 29.65%
[29 empty] | 2019 | December | 18 | 10 | 6227 | 28500 | 21.85%
[29 empty] | 2019 | December | 18 | 11 | 28069 | 28500 | 98.49%
[29 empty] | 2019 | December | 18 | 12 | 23627 | 28500 | 82.9%
[29 empty] | 2019 | December | 18 | 13 | 7962.5 | 28500 | 27.94%
[29 empty] | 2019 | December | 18 | 14 | 5459 | 28500 | 19.15%
[29 empty] | 2019 | December | 18 | 15 | 2081.5 | 28500 | 7.304%
[29 empty] | 2019 | December | 18 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 18 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 18 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 18 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 18 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 18 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 18 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 18 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 19 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 19 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 19 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 19 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 19 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 19 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 19 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 19 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 19 | 8 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 19 | 9 | 1979.5 | 28500 | 6.946%
[29 empty] | 2019 | December | 19 | 10 | 11474.5 | 28500 | 40.26%
[29 empty] | 2019 | December | 19 | 11 | 15552 | 28500 | 54.57%
[29 empty] | 2019 | December | 19 | 12 | 6675 | 28500 | 23.42%
[29 empty] | 2019 | December | 19 | 13 | 6731.5 | 28500 | 23.62%
[29 empty] | 2019 | December | 19 | 14 | 505.5 | 28500 | 1.774%
[29 empty] | 2019 | December | 19 | 15 | 117 | 28500 | 0.4105%
[29 empty] | 2019 | December | 19 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 19 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 19 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 19 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 19 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 19 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 19 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 19 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 20 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 20 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 20 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 20 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 20 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 20 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 20 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 20 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 20 | 8 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 20 | 9 | 95.5 | 28500 | 0.3351%
[29 empty] | 2019 | December | 20 | 10 | 804.5 | 28500 | 2.823%
[29 empty] | 2019 | December | 20 | 11 | 4404.5 | 28500 | 15.45%
[29 empty] | 2019 | December | 20 | 12 | 577 | 28500 | 2.025%
[29 empty] | 2019 | December | 20 | 13 | 1012 | 28500 | 3.551%
[29 empty] | 2019 | December | 20 | 14 | 15537 | 28500 | 54.52%
[29 empty] | 2019 | December | 20 | 15 | 7191 | 28500 | 25.23%
[29 empty] | 2019 | December | 20 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 20 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 20 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 20 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 20 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 20 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 20 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 20 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 21 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 21 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 21 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 21 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 21 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 21 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 21 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 21 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 21 | 8 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 21 | 9 | 33 | 28500 | 0.1158%
[29 empty] | 2019 | December | 21 | 10 | 25928.5 | 28500 | 90.98%
[29 empty] | 2019 | December | 21 | 11 | 17273.5 | 28500 | 60.61%
[29 empty] | 2019 | December | 21 | 12 | 19493 | 28500 | 68.4%
[29 empty] | 2019 | December | 21 | 13 | 3990 | 28500 | 14%
[29 empty] | 2019 | December | 21 | 14 | 169 | 28500 | 0.593%
[29 empty] | 2019 | December | 21 | 15 | 9844 | 28500 | 34.54%
[29 empty] | 2019 | December | 21 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 21 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 21 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 21 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 21 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 21 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 21 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 21 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 22 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 22 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 22 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 22 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 22 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 22 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 22 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 22 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 22 | 8 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 22 | 9 | 583.5 | 28500 | 2.047%
[29 empty] | 2019 | December | 22 | 10 | 7583 | 28500 | 26.61%
[29 empty] | 2019 | December | 22 | 11 | 26326 | 28500 | 92.37%
[29 empty] | 2019 | December | 22 | 12 | 23977.5 | 28500 | 84.13%
[29 empty] | 2019 | December | 22 | 13 | 12976 | 28500 | 45.53%
[29 empty] | 2019 | December | 22 | 14 | 4442.5 | 28500 | 15.59%
[29 empty] | 2019 | December | 22 | 15 | 2080.5 | 28500 | 7.3%
[29 empty] | 2019 | December | 22 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 22 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 22 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 22 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 22 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 22 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 22 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 22 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 23 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 23 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 23 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 23 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 23 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 23 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 23 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 23 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 23 | 8 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 23 | 9 | 13770.5 | 28500 | 48.32%
[29 empty] | 2019 | December | 23 | 10 | 23266 | 28500 | 81.64%
[29 empty] | 2019 | December | 23 | 11 | 28455.5 | 28500 | 99.84%
[29 empty] | 2019 | December | 23 | 12 | 27607.5 | 28500 | 96.87%
[29 empty] | 2019 | December | 23 | 13 | 20358.5 | 28500 | 71.43%
[29 empty] | 2019 | December | 23 | 14 | 8941.5 | 28500 | 31.37%
[29 empty] | 2019 | December | 23 | 15 | 10353.5 | 28500 | 36.33%
[29 empty] | 2019 | December | 23 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 23 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 23 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 23 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 23 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 23 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 23 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 23 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 24 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 24 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 24 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 24 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 24 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 24 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 24 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 24 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 24 | 8 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 24 | 9 | 10998 | 28500 | 38.59%
[29 empty] | 2019 | December | 24 | 10 | 2397 | 28500 | 8.411%
[29 empty] | 2019 | December | 24 | 11 | 25926.5 | 28500 | 90.97%
[29 empty] | 2019 | December | 24 | 12 | 13326.5 | 28500 | 46.76%
[29 empty] | 2019 | December | 24 | 13 | 17458.5 | 28500 | 61.26%
[29 empty] | 2019 | December | 24 | 14 | 2536 | 28500 | 8.898%
[29 empty] | 2019 | December | 24 | 15 | 5921 | 28500 | 20.78%
[29 empty] | 2019 | December | 24 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 24 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 24 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 24 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 24 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 24 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 24 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 24 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 25 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 25 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 25 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 25 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 25 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 25 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 25 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 25 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 25 | 8 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 25 | 9 | 13283.5 | 28500 | 46.61%
[29 empty] | 2019 | December | 25 | 10 | 22186.5 | 28500 | 77.85%
[29 empty] | 2019 | December | 25 | 11 | 28171.5 | 28500 | 98.85%
[29 empty] | 2019 | December | 25 | 12 | 28970.5 | 28500 | 101.7%
[29 empty] | 2019 | December | 25 | 13 | 25106.5 | 28500 | 88.09%
[29 empty] | 2019 | December | 25 | 14 | 19354.5 | 28500 | 67.91%
[29 empty] | 2019 | December | 25 | 15 | 8600.5 | 28500 | 30.18%
[29 empty] | 2019 | December | 25 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 25 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 25 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 25 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 25 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 25 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 25 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 25 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 26 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 26 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 26 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 26 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 26 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 26 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 26 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 26 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 26 | 8 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 26 | 9 | 4184.5 | 28500 | 14.68%
[29 empty] | 2019 | December | 26 | 10 | 4075.5 | 28500 | 14.3%
[29 empty] | 2019 | December | 26 | 11 | 6715 | 28500 | 23.56%
[29 empty] | 2019 | December | 26 | 12 | 10102.5 | 28500 | 35.45%
[29 empty] | 2019 | December | 26 | 13 | 1043.5 | 28500 | 3.661%
[29 empty] | 2019 | December | 26 | 14 | 1076.5 | 28500 | 3.777%
[29 empty] | 2019 | December | 26 | 15 | 596 | 28500 | 2.091%
[29 empty] | 2019 | December | 26 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 26 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 26 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 26 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 26 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 26 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 26 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 26 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 27 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 27 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 27 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 27 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 27 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 27 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 27 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 27 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 27 | 8 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 27 | 9 | 552.5 | 28500 | 1.939%
[29 empty] | 2019 | December | 27 | 10 | 8524 | 28500 | 29.91%
[29 empty] | 2019 | December | 27 | 11 | 19509 | 28500 | 68.45%
[29 empty] | 2019 | December | 27 | 12 | 21105 | 28500 | 74.05%
[29 empty] | 2019 | December | 27 | 13 | 11090 | 28500 | 38.91%
[29 empty] | 2019 | December | 27 | 14 | 2323 | 28500 | 8.151%
[29 empty] | 2019 | December | 27 | 15 | 1365 | 28500 | 4.789%
[29 empty] | 2019 | December | 27 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 27 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 27 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 27 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 27 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 27 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 27 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 27 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 28 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 28 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 28 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 28 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 28 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 28 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 28 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 28 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 28 | 8 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 28 | 9 | 1052 | 28500 | 3.691%
[29 empty] | 2019 | December | 28 | 10 | 810.5 | 28500 | 2.844%
[29 empty] | 2019 | December | 28 | 11 | 1544.5 | 28500 | 5.419%
[29 empty] | 2019 | December | 28 | 12 | 1182.5 | 28500 | 4.149%
[29 empty] | 2019 | December | 28 | 13 | 973 | 28500 | 3.414%
[29 empty] | 2019 | December | 28 | 14 | 391 | 28500 | 1.372%
[29 empty] | 2019 | December | 28 | 15 | 276 | 28500 | 0.9684%
[29 empty] | 2019 | December | 28 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 28 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 28 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 28 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 28 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 28 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 28 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 28 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 29 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 29 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 29 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 29 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 29 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 29 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 29 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 29 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 29 | 8 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 29 | 9 | 281 | 28500 | 0.986%
[29 empty] | 2019 | December | 29 | 10 | 4289 | 28500 | 15.05%
[29 empty] | 2019 | December | 29 | 11 | 13612.5 | 28500 | 47.76%
[29 empty] | 2019 | December | 29 | 12 | 20141.5 | 28500 | 70.67%
[29 empty] | 2019 | December | 29 | 13 | 26914.5 | 28500 | 94.44%
[29 empty] | 2019 | December | 29 | 14 | 16431.5 | 28500 | 57.65%
[29 empty] | 2019 | December | 29 | 15 | 8285 | 28500 | 29.07%
[29 empty] | 2019 | December | 29 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 29 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 29 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 29 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 29 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 29 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 29 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 29 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 30 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 30 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 30 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 30 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 30 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 30 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 30 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 30 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 30 | 8 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 30 | 9 | 11842.5 | 28500 | 41.55%
[29 empty] | 2019 | December | 30 | 10 | 22121.5 | 28500 | 77.62%
[29 empty] | 2019 | December | 30 | 11 | 28095.5 | 28500 | 98.58%
[29 empty] | 2019 | December | 30 | 12 | 29760.5 | 28500 | 104.4%
[29 empty] | 2019 | December | 30 | 13 | 26950.5 | 28500 | 94.56%
[29 empty] | 2019 | December | 30 | 14 | 20267 | 28500 | 71.11%
[29 empty] | 2019 | December | 30 | 15 | 9429 | 28500 | 33.08%
[29 empty] | 2019 | December | 30 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 30 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 30 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 30 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 30 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 30 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 30 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 30 | 23 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 31 | 24 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 31 | 1 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 31 | 2 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 31 | 3 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 31 | 4 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 31 | 5 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 31 | 6 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 31 | 7 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 31 | 8 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 31 | 9 | 2955.5 | 28500 | 10.37%
[29 empty] | 2019 | December | 31 | 10 | 711 | 28500 | 2.495%
[29 empty] | 2019 | December | 31 | 11 | 1543.5 | 28500 | 5.416%
[29 empty] | 2019 | December | 31 | 12 | 576 | 28500 | 2.021%
[29 empty] | 2019 | December | 31 | 13 | 672 | 28500 | 2.358%
[29 empty] | 2019 | December | 31 | 14 | 576 | 28500 | 2.021%
[29 empty] | 2019 | December | 31 | 15 | 276 | 28500 | 0.9684%
[29 empty] | 2019 | December | 31 | 16 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 31 | 17 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 31 | 18 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 31 | 19 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 31 | 20 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 31 | 21 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 31 | 22 | 0 | 28500 | 0%
[29 empty] | 2019 | December | 31 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 1 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 1 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 1 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 1 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 1 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 1 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 1 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 1 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 1 | 8 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 1 | 9 | 689 | 28500 | 2.418%
[29 empty] | 2020 | January | 1 | 10 | 2393.5 | 28500 | 8.398%
[29 empty] | 2020 | January | 1 | 11 | 1681 | 28500 | 5.898%
[29 empty] | 2020 | January | 1 | 12 | 1865 | 28500 | 6.544%
[29 empty] | 2020 | January | 1 | 13 | 1417.5 | 28500 | 4.974%
[29 empty] | 2020 | January | 1 | 14 | 816.5 | 28500 | 2.865%
[29 empty] | 2020 | January | 1 | 15 | 643 | 28500 | 2.256%
[29 empty] | 2020 | January | 1 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 1 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 1 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 1 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 1 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 1 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 1 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 1 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 2 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 2 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 2 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 2 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 2 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 2 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 2 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 2 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 2 | 8 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 2 | 9 | 74.5 | 28500 | 0.2614%
[29 empty] | 2020 | January | 2 | 10 | 1401.5 | 28500 | 4.918%
[29 empty] | 2020 | January | 2 | 11 | 3685 | 28500 | 12.93%
[29 empty] | 2020 | January | 2 | 12 | 6053 | 28500 | 21.24%
[29 empty] | 2020 | January | 2 | 13 | 3870 | 28500 | 13.58%
[29 empty] | 2020 | January | 2 | 14 | 936.5 | 28500 | 3.286%
[29 empty] | 2020 | January | 2 | 15 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 2 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 2 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 2 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 2 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 2 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 2 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 2 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 2 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 3 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 3 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 3 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 3 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 3 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 3 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 3 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 3 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 3 | 8 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 3 | 9 | 5455.5 | 28500 | 19.14%
[29 empty] | 2020 | January | 3 | 10 | 194 | 28500 | 0.6807%
[29 empty] | 2020 | January | 3 | 11 | 16779 | 28500 | 58.87%
[29 empty] | 2020 | January | 3 | 12 | 2451 | 28500 | 8.6%
[29 empty] | 2020 | January | 3 | 13 | 1553.5 | 28500 | 5.451%
[29 empty] | 2020 | January | 3 | 14 | 20087 | 28500 | 70.48%
[29 empty] | 2020 | January | 3 | 15 | 11210 | 28500 | 39.33%
[29 empty] | 2020 | January | 3 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 3 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 3 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 3 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 3 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 3 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 3 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 3 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 4 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 4 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 4 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 4 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 4 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 4 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 4 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 4 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 4 | 8 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 4 | 9 | 13567.5 | 28500 | 47.61%
[29 empty] | 2020 | January | 4 | 10 | 14822 | 28500 | 52.01%
[29 empty] | 2020 | January | 4 | 11 | 4113.5 | 28500 | 14.43%
[29 empty] | 2020 | January | 4 | 12 | 12737.5 | 28500 | 44.69%
[29 empty] | 2020 | January | 4 | 13 | 27087.5 | 28500 | 95.04%
[29 empty] | 2020 | January | 4 | 14 | 21759 | 28500 | 76.35%
[29 empty] | 2020 | January | 4 | 15 | 10070 | 28500 | 35.33%
[29 empty] | 2020 | January | 4 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 4 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 4 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 4 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 4 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 4 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 4 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 4 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 5 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 5 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 5 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 5 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 5 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 5 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 5 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 5 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 5 | 8 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 5 | 9 | 2062.5 | 28500 | 7.237%
[29 empty] | 2020 | January | 5 | 10 | 2795.5 | 28500 | 9.809%
[29 empty] | 2020 | January | 5 | 11 | 6430 | 28500 | 22.56%
[29 empty] | 2020 | January | 5 | 12 | 1773.5 | 28500 | 6.223%
[29 empty] | 2020 | January | 5 | 13 | 1476 | 28500 | 5.179%
[29 empty] | 2020 | January | 5 | 14 | 1329.5 | 28500 | 4.665%
[29 empty] | 2020 | January | 5 | 15 | 856 | 28500 | 3.004%
[29 empty] | 2020 | January | 5 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 5 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 5 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 5 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 5 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 5 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 5 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 5 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 6 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 6 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 6 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 6 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 6 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 6 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 6 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 6 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 6 | 8 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 6 | 9 | 1112.5 | 28500 | 3.904%
[29 empty] | 2020 | January | 6 | 10 | 9304 | 28500 | 32.65%
[29 empty] | 2020 | January | 6 | 11 | 16963.5 | 28500 | 59.52%
[29 empty] | 2020 | January | 6 | 12 | 28007.5 | 28500 | 98.27%
[29 empty] | 2020 | January | 6 | 13 | 2616 | 28500 | 9.179%
[29 empty] | 2020 | January | 6 | 14 | 24321 | 28500 | 85.34%
[29 empty] | 2020 | January | 6 | 15 | 1521 | 28500 | 5.337%
[29 empty] | 2020 | January | 6 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 6 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 6 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 6 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 6 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 6 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 6 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 6 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 7 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 7 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 7 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 7 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 7 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 7 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 7 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 7 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 7 | 8 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 7 | 9 | 485.5 | 28500 | 1.704%
[29 empty] | 2020 | January | 7 | 10 | 2714.5 | 28500 | 9.525%
[29 empty] | 2020 | January | 7 | 11 | 972 | 28500 | 3.411%
[29 empty] | 2020 | January | 7 | 12 | 25551 | 28500 | 89.65%
[29 empty] | 2020 | January | 7 | 13 | 23396.5 | 28500 | 82.09%
[29 empty] | 2020 | January | 7 | 14 | 13681 | 28500 | 48%
[29 empty] | 2020 | January | 7 | 15 | 2695 | 28500 | 9.456%
[29 empty] | 2020 | January | 7 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 7 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 7 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 7 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 7 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 7 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 7 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 7 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 8 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 8 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 8 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 8 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 8 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 8 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 8 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 8 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 8 | 8 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 8 | 9 | 1081.5 | 28500 | 3.795%
[29 empty] | 2020 | January | 8 | 10 | 2425.5 | 28500 | 8.511%
[29 empty] | 2020 | January | 8 | 11 | 5998.5 | 28500 | 21.05%
[29 empty] | 2020 | January | 8 | 12 | 10266.5 | 28500 | 36.02%
[29 empty] | 2020 | January | 8 | 13 | 6110 | 28500 | 21.44%
[29 empty] | 2020 | January | 8 | 14 | 1310 | 28500 | 4.596%
[29 empty] | 2020 | January | 8 | 15 | 796.5 | 28500 | 2.795%
[29 empty] | 2020 | January | 8 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 8 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 8 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 8 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 8 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 8 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 8 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 8 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 9 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 9 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 9 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 9 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 9 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 9 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 9 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 9 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 9 | 8 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 9 | 9 | 15148.5 | 28500 | 53.15%
[29 empty] | 2020 | January | 9 | 10 | 12768.5 | 28500 | 44.8%
[29 empty] | 2020 | January | 9 | 11 | 22628 | 28500 | 79.4%
[29 empty] | 2020 | January | 9 | 12 | 25744 | 28500 | 90.33%
[29 empty] | 2020 | January | 9 | 13 | 10530.5 | 28500 | 36.95%
[29 empty] | 2020 | January | 9 | 14 | 4194 | 28500 | 14.72%
[29 empty] | 2020 | January | 9 | 15 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 9 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 9 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 9 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 9 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 9 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 9 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 9 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 9 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 10 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 10 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 10 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 10 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 10 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 10 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 10 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 10 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 10 | 8 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 10 | 9 | 1480 | 28500 | 5.193%
[29 empty] | 2020 | January | 10 | 10 | 3201 | 28500 | 11.23%
[29 empty] | 2020 | January | 10 | 11 | 4193 | 28500 | 14.71%
[29 empty] | 2020 | January | 10 | 12 | 3952.5 | 28500 | 13.87%
[29 empty] | 2020 | January | 10 | 13 | 18958.5 | 28500 | 66.52%
[29 empty] | 2020 | January | 10 | 14 | 23900 | 28500 | 83.86%
[29 empty] | 2020 | January | 10 | 15 | 11712 | 28500 | 41.09%
[29 empty] | 2020 | January | 10 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 10 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 10 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 10 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 10 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 10 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 10 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 10 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 11 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 11 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 11 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 11 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 11 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 11 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 11 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 11 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 11 | 8 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 11 | 9 | 1493 | 28500 | 5.239%
[29 empty] | 2020 | January | 11 | 10 | 2081.5 | 28500 | 7.304%
[29 empty] | 2020 | January | 11 | 11 | 5592.5 | 28500 | 19.62%
[29 empty] | 2020 | January | 11 | 12 | 13050 | 28500 | 45.79%
[29 empty] | 2020 | January | 11 | 13 | 5945.5 | 28500 | 20.86%
[29 empty] | 2020 | January | 11 | 14 | 702.5 | 28500 | 2.465%
[29 empty] | 2020 | January | 11 | 15 | 2160 | 28500 | 7.579%
[29 empty] | 2020 | January | 11 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 11 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 11 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 11 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 11 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 11 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 11 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 11 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 12 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 12 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 12 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 12 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 12 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 12 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 12 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 12 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 12 | 8 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 12 | 9 | 3765.5 | 28500 | 13.21%
[29 empty] | 2020 | January | 12 | 10 | 7219 | 28500 | 25.33%
[29 empty] | 2020 | January | 12 | 11 | 16864 | 28500 | 59.17%
[29 empty] | 2020 | January | 12 | 12 | 10234 | 28500 | 35.91%
[29 empty] | 2020 | January | 12 | 13 | 20289.5 | 28500 | 71.19%
[29 empty] | 2020 | January | 12 | 14 | 13183.5 | 28500 | 46.26%
[29 empty] | 2020 | January | 12 | 15 | 11616 | 28500 | 40.76%
[29 empty] | 2020 | January | 12 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 12 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 12 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 12 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 12 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 12 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 12 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 12 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 13 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 13 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 13 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 13 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 13 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 13 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 13 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 13 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 13 | 8 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 13 | 9 | 3772.5 | 28500 | 13.24%
[29 empty] | 2020 | January | 13 | 10 | 12374.5 | 28500 | 43.42%
[29 empty] | 2020 | January | 13 | 11 | 13371 | 28500 | 46.92%
[29 empty] | 2020 | January | 13 | 12 | 6536.5 | 28500 | 22.94%
[29 empty] | 2020 | January | 13 | 13 | 1009.5 | 28500 | 3.542%
[29 empty] | 2020 | January | 13 | 14 | 2118.5 | 28500 | 7.433%
[29 empty] | 2020 | January | 13 | 15 | 362 | 28500 | 1.27%
[29 empty] | 2020 | January | 13 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 13 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 13 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 13 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 13 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 13 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 13 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 13 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 14 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 14 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 14 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 14 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 14 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 14 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 14 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 14 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 14 | 8 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 14 | 9 | 423 | 28500 | 1.484%
[29 empty] | 2020 | January | 14 | 10 | 1112 | 28500 | 3.902%
[29 empty] | 2020 | January | 14 | 11 | 4913 | 28500 | 17.24%
[29 empty] | 2020 | January | 14 | 12 | 2614.5 | 28500 | 9.174%
[29 empty] | 2020 | January | 14 | 13 | 2642.5 | 28500 | 9.272%
[29 empty] | 2020 | January | 14 | 14 | 2444.5 | 28500 | 8.577%
[29 empty] | 2020 | January | 14 | 15 | 243 | 28500 | 0.8526%
[29 empty] | 2020 | January | 14 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 14 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 14 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 14 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 14 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 14 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 14 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 14 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 15 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 15 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 15 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 15 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 15 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 15 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 15 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 15 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 15 | 8 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 15 | 9 | 1180 | 28500 | 4.14%
[29 empty] | 2020 | January | 15 | 10 | 250.5 | 28500 | 0.8789%
[29 empty] | 2020 | January | 15 | 11 | 4061 | 28500 | 14.25%
[29 empty] | 2020 | January | 15 | 12 | 4919.5 | 28500 | 17.26%
[29 empty] | 2020 | January | 15 | 13 | 24865.5 | 28500 | 87.25%
[29 empty] | 2020 | January | 15 | 14 | 17682.5 | 28500 | 62.04%
[29 empty] | 2020 | January | 15 | 15 | 12226 | 28500 | 42.9%
[29 empty] | 2020 | January | 15 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 15 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 15 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 15 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 15 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 15 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 15 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 15 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 16 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 16 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 16 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 16 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 16 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 16 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 16 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 16 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 16 | 8 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 16 | 9 | 2622.5 | 28500 | 9.202%
[29 empty] | 2020 | January | 16 | 10 | 2312.5 | 28500 | 8.114%
[29 empty] | 2020 | January | 16 | 11 | 1658.5 | 28500 | 5.819%
[29 empty] | 2020 | January | 16 | 12 | 24130 | 28500 | 84.67%
[29 empty] | 2020 | January | 16 | 13 | 20344.5 | 28500 | 71.38%
[29 empty] | 2020 | January | 16 | 14 | 9637 | 28500 | 33.81%
[29 empty] | 2020 | January | 16 | 15 | 7212.5 | 28500 | 25.31%
[29 empty] | 2020 | January | 16 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 16 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 16 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 16 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 16 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 16 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 16 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 16 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 17 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 17 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 17 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 17 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 17 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 17 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 17 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 17 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 17 | 8 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 17 | 9 | 775.5 | 28500 | 2.721%
[29 empty] | 2020 | January | 17 | 10 | 16824 | 28500 | 59.03%
[29 empty] | 2020 | January | 17 | 11 | 1400 | 28500 | 4.912%
[29 empty] | 2020 | January | 17 | 12 | 21723 | 28500 | 76.22%
[29 empty] | 2020 | January | 17 | 13 | 5630 | 28500 | 19.75%
[29 empty] | 2020 | January | 17 | 14 | 10418 | 28500 | 36.55%
[29 empty] | 2020 | January | 17 | 15 | 847.5 | 28500 | 2.974%
[29 empty] | 2020 | January | 17 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 17 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 17 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 17 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 17 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 17 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 17 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 17 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 18 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 18 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 18 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 18 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 18 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 18 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 18 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 18 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 18 | 8 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 18 | 9 | 10412.5 | 28500 | 36.54%
[29 empty] | 2020 | January | 18 | 10 | 25527 | 28500 | 89.57%
[29 empty] | 2020 | January | 18 | 11 | 30909.5 | 28500 | 108.5%
[29 empty] | 2020 | January | 18 | 12 | 33521 | 28500 | 117.6%
[29 empty] | 2020 | January | 18 | 13 | 31578 | 28500 | 110.8%
[29 empty] | 2020 | January | 18 | 14 | 26266.5 | 28500 | 92.16%
[29 empty] | 2020 | January | 18 | 15 | 15325.5 | 28500 | 53.77%
[29 empty] | 2020 | January | 18 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 18 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 18 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 18 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 18 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 18 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 18 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 18 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 19 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 19 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 19 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 19 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 19 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 19 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 19 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 19 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 19 | 8 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 19 | 9 | 9481.5 | 28500 | 33.27%
[29 empty] | 2020 | January | 19 | 10 | 24696 | 28500 | 86.65%
[29 empty] | 2020 | January | 19 | 11 | 30292.5 | 28500 | 106.3%
[29 empty] | 2020 | January | 19 | 12 | 33117 | 28500 | 116.2%
[29 empty] | 2020 | January | 19 | 13 | 29740 | 28500 | 104.4%
[29 empty] | 2020 | January | 19 | 14 | 25202 | 28500 | 88.43%
[29 empty] | 2020 | January | 19 | 15 | 15929.5 | 28500 | 55.89%
[29 empty] | 2020 | January | 19 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 19 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 19 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 19 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 19 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 19 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 19 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 19 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 20 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 20 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 20 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 20 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 20 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 20 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 20 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 20 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 20 | 8 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 20 | 9 | 8722 | 28500 | 30.6%
[29 empty] | 2020 | January | 20 | 10 | 4311 | 28500 | 15.13%
[29 empty] | 2020 | January | 20 | 11 | 7369.5 | 28500 | 25.86%
[29 empty] | 2020 | January | 20 | 12 | 8344 | 28500 | 29.28%
[29 empty] | 2020 | January | 20 | 13 | 4594 | 28500 | 16.12%
[29 empty] | 2020 | January | 20 | 14 | 23135.5 | 28500 | 81.18%
[29 empty] | 2020 | January | 20 | 15 | 15375 | 28500 | 53.95%
[29 empty] | 2020 | January | 20 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 20 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 20 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 20 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 20 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 20 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 20 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 20 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 21 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 21 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 21 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 21 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 21 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 21 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 21 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 21 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 21 | 8 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 21 | 9 | 9287 | 28500 | 32.59%
[29 empty] | 2020 | January | 21 | 10 | 5903.5 | 28500 | 20.71%
[29 empty] | 2020 | January | 21 | 11 | 13277 | 28500 | 46.59%
[29 empty] | 2020 | January | 21 | 12 | 31860.5 | 28500 | 111.8%
[29 empty] | 2020 | January | 21 | 13 | 29491.5 | 28500 | 103.5%
[29 empty] | 2020 | January | 21 | 14 | 24473 | 28500 | 85.87%
[29 empty] | 2020 | January | 21 | 15 | 15387 | 28500 | 53.99%
[29 empty] | 2020 | January | 21 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 21 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 21 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 21 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 21 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 21 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 21 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 21 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 22 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 22 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 22 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 22 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 22 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 22 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 22 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 22 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 22 | 8 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 22 | 9 | 625.5 | 28500 | 2.195%
[29 empty] | 2020 | January | 22 | 10 | 1351 | 28500 | 4.74%
[29 empty] | 2020 | January | 22 | 11 | 1417.5 | 28500 | 4.974%
[29 empty] | 2020 | January | 22 | 12 | 1671 | 28500 | 5.863%
[29 empty] | 2020 | January | 22 | 13 | 1374.5 | 28500 | 4.823%
[29 empty] | 2020 | January | 22 | 14 | 519 | 28500 | 1.821%
[29 empty] | 2020 | January | 22 | 15 | 279 | 28500 | 0.9789%
[29 empty] | 2020 | January | 22 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 22 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 22 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 22 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 22 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 22 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 22 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 22 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 23 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 23 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 23 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 23 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 23 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 23 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 23 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 23 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 23 | 8 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 23 | 9 | 521.5 | 28500 | 1.83%
[29 empty] | 2020 | January | 23 | 10 | 1412.5 | 28500 | 4.956%
[29 empty] | 2020 | January | 23 | 11 | 1814 | 28500 | 6.365%
[29 empty] | 2020 | January | 23 | 12 | 2226 | 28500 | 7.811%
[29 empty] | 2020 | January | 23 | 13 | 1552 | 28500 | 5.446%
[29 empty] | 2020 | January | 23 | 14 | 1050.5 | 28500 | 3.686%
[29 empty] | 2020 | January | 23 | 15 | 947 | 28500 | 3.323%
[29 empty] | 2020 | January | 23 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 23 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 23 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 23 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 23 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 23 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 23 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 23 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 24 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 24 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 24 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 24 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 24 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 24 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 24 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 24 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 24 | 8 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 24 | 9 | 461.5 | 28500 | 1.619%
[29 empty] | 2020 | January | 24 | 10 | 1308.5 | 28500 | 4.591%
[29 empty] | 2020 | January | 24 | 11 | 1413 | 28500 | 4.958%
[29 empty] | 2020 | January | 24 | 12 | 1850.5 | 28500 | 6.493%
[29 empty] | 2020 | January | 24 | 13 | 2186.5 | 28500 | 7.672%
[29 empty] | 2020 | January | 24 | 14 | 914 | 28500 | 3.207%
[29 empty] | 2020 | January | 24 | 15 | 550 | 28500 | 1.93%
[29 empty] | 2020 | January | 24 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 24 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 24 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 24 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 24 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 24 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 24 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 24 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 25 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 25 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 25 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 25 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 25 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 25 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 25 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 25 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 25 | 8 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 25 | 9 | 722.5 | 28500 | 2.535%
[29 empty] | 2020 | January | 25 | 10 | 1458.5 | 28500 | 5.118%
[29 empty] | 2020 | January | 25 | 11 | 1974 | 28500 | 6.926%
[29 empty] | 2020 | January | 25 | 12 | 1855.5 | 28500 | 6.511%
[29 empty] | 2020 | January | 25 | 13 | 1928.5 | 28500 | 6.767%
[29 empty] | 2020 | January | 25 | 14 | 1519.5 | 28500 | 5.332%
[29 empty] | 2020 | January | 25 | 15 | 2062 | 28500 | 7.235%
[29 empty] | 2020 | January | 25 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 25 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 25 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 25 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 25 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 25 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 25 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 25 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 26 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 26 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 26 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 26 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 26 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 26 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 26 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 26 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 26 | 8 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 26 | 9 | 1016.5 | 28500 | 3.567%
[29 empty] | 2020 | January | 26 | 10 | 3634 | 28500 | 12.75%
[29 empty] | 2020 | January | 26 | 11 | 5277.5 | 28500 | 18.52%
[29 empty] | 2020 | January | 26 | 12 | 5603 | 28500 | 19.66%
[29 empty] | 2020 | January | 26 | 13 | 5988.5 | 28500 | 21.01%
[29 empty] | 2020 | January | 26 | 14 | 2167 | 28500 | 7.604%
[29 empty] | 2020 | January | 26 | 15 | 974 | 28500 | 3.418%
[29 empty] | 2020 | January | 26 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 26 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 26 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 26 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 26 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 26 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 26 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 26 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 27 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 27 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 27 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 27 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 27 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 27 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 27 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 27 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 27 | 8 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 27 | 9 | 1231.5 | 28500 | 4.321%
[29 empty] | 2020 | January | 27 | 10 | 12086.5 | 28500 | 42.41%
[29 empty] | 2020 | January | 27 | 11 | 33201 | 28500 | 116.5%
[29 empty] | 2020 | January | 27 | 12 | 10169.5 | 28500 | 35.68%
[29 empty] | 2020 | January | 27 | 13 | 3541.5 | 28500 | 12.43%
[29 empty] | 2020 | January | 27 | 14 | 4252 | 28500 | 14.92%
[29 empty] | 2020 | January | 27 | 15 | 1086.5 | 28500 | 3.812%
[29 empty] | 2020 | January | 27 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 27 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 27 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 27 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 27 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 27 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 27 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 27 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 28 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 28 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 28 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 28 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 28 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 28 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 28 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 28 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 28 | 8 | 418.5 | 28500 | 1.468%
[29 empty] | 2020 | January | 28 | 9 | 16655 | 28500 | 58.44%
[29 empty] | 2020 | January | 28 | 10 | 18113.5 | 28500 | 63.56%
[29 empty] | 2020 | January | 28 | 11 | 32157.5 | 28500 | 112.8%
[29 empty] | 2020 | January | 28 | 12 | 36426 | 28500 | 127.8%
[29 empty] | 2020 | January | 28 | 13 | 33725 | 28500 | 118.3%
[29 empty] | 2020 | January | 28 | 14 | 27066.5 | 28500 | 94.97%
[29 empty] | 2020 | January | 28 | 15 | 20257.5 | 28500 | 71.08%
[29 empty] | 2020 | January | 28 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 28 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 28 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 28 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 28 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 28 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 28 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 28 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 29 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 29 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 29 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 29 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 29 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 29 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 29 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 29 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 29 | 8 | 431 | 28500 | 1.512%
[29 empty] | 2020 | January | 29 | 9 | 6518.5 | 28500 | 22.87%
[29 empty] | 2020 | January | 29 | 10 | 29050.5 | 28500 | 101.9%
[29 empty] | 2020 | January | 29 | 11 | 27875.5 | 28500 | 97.81%
[29 empty] | 2020 | January | 29 | 12 | 36411 | 28500 | 127.8%
[29 empty] | 2020 | January | 29 | 13 | 34174.5 | 28500 | 119.9%
[29 empty] | 2020 | January | 29 | 14 | 14405 | 28500 | 50.54%
[29 empty] | 2020 | January | 29 | 15 | 14034.5 | 28500 | 49.24%
[29 empty] | 2020 | January | 29 | 16 | 1020.5 | 28500 | 3.581%
[29 empty] | 2020 | January | 29 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 29 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 29 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 29 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 29 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 29 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 29 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 30 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 30 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 30 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 30 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 30 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 30 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 30 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 30 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 30 | 8 | 32.5 | 28500 | 0.114%
[29 empty] | 2020 | January | 30 | 9 | 2230 | 28500 | 7.825%
[29 empty] | 2020 | January | 30 | 10 | 1291 | 28500 | 4.53%
[29 empty] | 2020 | January | 30 | 11 | 706 | 28500 | 2.477%
[29 empty] | 2020 | January | 30 | 12 | 7158.5 | 28500 | 25.12%
[29 empty] | 2020 | January | 30 | 13 | 6645.5 | 28500 | 23.32%
[29 empty] | 2020 | January | 30 | 14 | 1494.5 | 28500 | 5.244%
[29 empty] | 2020 | January | 30 | 15 | 667 | 28500 | 2.34%
[29 empty] | 2020 | January | 30 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 30 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 30 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 30 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 30 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 30 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 30 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 30 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 31 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 31 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 31 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 31 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 31 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 31 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 31 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 31 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 31 | 8 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 31 | 9 | 869 | 28500 | 3.049%
[29 empty] | 2020 | January | 31 | 10 | 604.5 | 28500 | 2.121%
[29 empty] | 2020 | January | 31 | 11 | 4703 | 28500 | 16.5%
[29 empty] | 2020 | January | 31 | 12 | 15573 | 28500 | 54.64%
[29 empty] | 2020 | January | 31 | 13 | 4116.5 | 28500 | 14.44%
[29 empty] | 2020 | January | 31 | 14 | 2863.5 | 28500 | 10.05%
[29 empty] | 2020 | January | 31 | 15 | 636 | 28500 | 2.232%
[29 empty] | 2020 | January | 31 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 31 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 31 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 31 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 31 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 31 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 31 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | January | 31 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 1 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 1 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 1 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 1 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 1 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 1 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 1 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 1 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 1 | 8 | 733 | 28500 | 2.572%
[29 empty] | 2020 | February | 1 | 9 | 17458.5 | 28500 | 61.26%
[29 empty] | 2020 | February | 1 | 10 | 25343 | 28500 | 88.92%
[29 empty] | 2020 | February | 1 | 11 | 14370 | 28500 | 50.42%
[29 empty] | 2020 | February | 1 | 12 | 10001 | 28500 | 35.09%
[29 empty] | 2020 | February | 1 | 13 | 24146 | 28500 | 84.72%
[29 empty] | 2020 | February | 1 | 14 | 24940 | 28500 | 87.51%
[29 empty] | 2020 | February | 1 | 15 | 14726 | 28500 | 51.67%
[29 empty] | 2020 | February | 1 | 16 | 5277 | 28500 | 18.52%
[29 empty] | 2020 | February | 1 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 1 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 1 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 1 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 1 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 1 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 1 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 2 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 2 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 2 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 2 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 2 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 2 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 2 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 2 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 2 | 8 | 479.5 | 28500 | 1.682%
[29 empty] | 2020 | February | 2 | 9 | 2877.5 | 28500 | 10.1%
[29 empty] | 2020 | February | 2 | 10 | 8631.5 | 28500 | 30.29%
[29 empty] | 2020 | February | 2 | 11 | 15940 | 28500 | 55.93%
[29 empty] | 2020 | February | 2 | 12 | 14695.5 | 28500 | 51.56%
[29 empty] | 2020 | February | 2 | 13 | 22244.5 | 28500 | 78.05%
[29 empty] | 2020 | February | 2 | 14 | 2362.5 | 28500 | 8.289%
[29 empty] | 2020 | February | 2 | 15 | 2262 | 28500 | 7.937%
[29 empty] | 2020 | February | 2 | 16 | 191.5 | 28500 | 0.6719%
[29 empty] | 2020 | February | 2 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 2 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 2 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 2 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 2 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 2 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 2 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 3 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 3 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 3 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 3 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 3 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 3 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 3 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 3 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 3 | 8 | 5672.5 | 28500 | 19.9%
[29 empty] | 2020 | February | 3 | 9 | 16099.5 | 28500 | 56.49%
[29 empty] | 2020 | February | 3 | 10 | 17427 | 28500 | 61.15%
[29 empty] | 2020 | February | 3 | 11 | 14276.5 | 28500 | 50.09%
[29 empty] | 2020 | February | 3 | 12 | 23154.5 | 28500 | 81.24%
[29 empty] | 2020 | February | 3 | 13 | 2084 | 28500 | 7.312%
[29 empty] | 2020 | February | 3 | 14 | 6419 | 28500 | 22.52%
[29 empty] | 2020 | February | 3 | 15 | 3422 | 28500 | 12.01%
[29 empty] | 2020 | February | 3 | 16 | 276.5 | 28500 | 0.9702%
[29 empty] | 2020 | February | 3 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 3 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 3 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 3 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 3 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 3 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 3 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 4 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 4 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 4 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 4 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 4 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 4 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 4 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 4 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 4 | 8 | 6796 | 28500 | 23.85%
[29 empty] | 2020 | February | 4 | 9 | 14495 | 28500 | 50.86%
[29 empty] | 2020 | February | 4 | 10 | 21135 | 28500 | 74.16%
[29 empty] | 2020 | February | 4 | 11 | 8434.5 | 28500 | 29.59%
[29 empty] | 2020 | February | 4 | 12 | 7140 | 28500 | 25.05%
[29 empty] | 2020 | February | 4 | 13 | 2420.5 | 28500 | 8.493%
[29 empty] | 2020 | February | 4 | 14 | 1659.5 | 28500 | 5.823%
[29 empty] | 2020 | February | 4 | 15 | 1655 | 28500 | 5.807%
[29 empty] | 2020 | February | 4 | 16 | 195 | 28500 | 0.6842%
[29 empty] | 2020 | February | 4 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 4 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 4 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 4 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 4 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 4 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 4 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 5 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 5 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 5 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 5 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 5 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 5 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 5 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 5 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 5 | 8 | 1638.5 | 28500 | 5.749%
[29 empty] | 2020 | February | 5 | 9 | 11058 | 28500 | 38.8%
[29 empty] | 2020 | February | 5 | 10 | 23052 | 28500 | 80.88%
[29 empty] | 2020 | February | 5 | 11 | 30249.5 | 28500 | 106.1%
[29 empty] | 2020 | February | 5 | 12 | 35425 | 28500 | 124.3%
[29 empty] | 2020 | February | 5 | 13 | 28544 | 28500 | 100.2%
[29 empty] | 2020 | February | 5 | 14 | 15444.5 | 28500 | 54.19%
[29 empty] | 2020 | February | 5 | 15 | 17701.5 | 28500 | 62.11%
[29 empty] | 2020 | February | 5 | 16 | 8273 | 28500 | 29.03%
[29 empty] | 2020 | February | 5 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 5 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 5 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 5 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 5 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 5 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 5 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 6 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 6 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 6 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 6 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 6 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 6 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 6 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 6 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 6 | 8 | 6786 | 28500 | 23.81%
[29 empty] | 2020 | February | 6 | 9 | 15384 | 28500 | 53.98%
[29 empty] | 2020 | February | 6 | 10 | 29208.5 | 28500 | 102.5%
[29 empty] | 2020 | February | 6 | 11 | 29294 | 28500 | 102.8%
[29 empty] | 2020 | February | 6 | 12 | 35287.5 | 28500 | 123.8%
[29 empty] | 2020 | February | 6 | 13 | 34194.5 | 28500 | 120%
[29 empty] | 2020 | February | 6 | 14 | 29813 | 28500 | 104.6%
[29 empty] | 2020 | February | 6 | 15 | 19308 | 28500 | 67.75%
[29 empty] | 2020 | February | 6 | 16 | 7996 | 28500 | 28.06%
[29 empty] | 2020 | February | 6 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 6 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 6 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 6 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 6 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 6 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 6 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 7 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 7 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 7 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 7 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 7 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 7 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 7 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 7 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 7 | 8 | 6853 | 28500 | 24.05%
[29 empty] | 2020 | February | 7 | 9 | 16016.5 | 28500 | 56.2%
[29 empty] | 2020 | February | 7 | 10 | 30308.5 | 28500 | 106.3%
[29 empty] | 2020 | February | 7 | 11 | 32619 | 28500 | 114.5%
[29 empty] | 2020 | February | 7 | 12 | 36983.5 | 28500 | 129.8%
[29 empty] | 2020 | February | 7 | 13 | 19666 | 28500 | 69%
[29 empty] | 2020 | February | 7 | 14 | 19535.5 | 28500 | 68.55%
[29 empty] | 2020 | February | 7 | 15 | 8802.5 | 28500 | 30.89%
[29 empty] | 2020 | February | 7 | 16 | 33 | 28500 | 0.1158%
[29 empty] | 2020 | February | 7 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 7 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 7 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 7 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 7 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 7 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 7 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 8 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 8 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 8 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 8 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 8 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 8 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 8 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 8 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 8 | 8 | 1169.5 | 28500 | 4.104%
[29 empty] | 2020 | February | 8 | 9 | 2134 | 28500 | 7.488%
[29 empty] | 2020 | February | 8 | 10 | 12011 | 28500 | 42.14%
[29 empty] | 2020 | February | 8 | 11 | 15060.5 | 28500 | 52.84%
[29 empty] | 2020 | February | 8 | 12 | 22014 | 28500 | 77.24%
[29 empty] | 2020 | February | 8 | 13 | 36163 | 28500 | 126.9%
[29 empty] | 2020 | February | 8 | 14 | 31178.5 | 28500 | 109.4%
[29 empty] | 2020 | February | 8 | 15 | 20402.5 | 28500 | 71.59%
[29 empty] | 2020 | February | 8 | 16 | 9800 | 28500 | 34.39%
[29 empty] | 2020 | February | 8 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 8 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 8 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 8 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 8 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 8 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 8 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 9 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 9 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 9 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 9 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 9 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 9 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 9 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 9 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 9 | 8 | 168 | 28500 | 0.5895%
[29 empty] | 2020 | February | 9 | 9 | 1003.5 | 28500 | 3.521%
[29 empty] | 2020 | February | 9 | 10 | 3156.5 | 28500 | 11.08%
[29 empty] | 2020 | February | 9 | 11 | 2415.5 | 28500 | 8.475%
[29 empty] | 2020 | February | 9 | 12 | 2370.5 | 28500 | 8.318%
[29 empty] | 2020 | February | 9 | 13 | 1339.5 | 28500 | 4.7%
[29 empty] | 2020 | February | 9 | 14 | 1376.5 | 28500 | 4.83%
[29 empty] | 2020 | February | 9 | 15 | 629.5 | 28500 | 2.209%
[29 empty] | 2020 | February | 9 | 16 | 858.5 | 28500 | 3.012%
[29 empty] | 2020 | February | 9 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 9 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 9 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 9 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 9 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 9 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 9 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 10 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 10 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 10 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 10 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 10 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 10 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 10 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 10 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 10 | 8 | 9156.5 | 28500 | 32.13%
[29 empty] | 2020 | February | 10 | 9 | 12463 | 28500 | 43.73%
[29 empty] | 2020 | February | 10 | 10 | 28988 | 28500 | 101.7%
[29 empty] | 2020 | February | 10 | 11 | 19462 | 28500 | 68.29%
[29 empty] | 2020 | February | 10 | 12 | 25024 | 28500 | 87.8%
[29 empty] | 2020 | February | 10 | 13 | 3531 | 28500 | 12.39%
[29 empty] | 2020 | February | 10 | 14 | 13206.5 | 28500 | 46.34%
[29 empty] | 2020 | February | 10 | 15 | 2988 | 28500 | 10.48%
[29 empty] | 2020 | February | 10 | 16 | 75 | 28500 | 0.2632%
[29 empty] | 2020 | February | 10 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 10 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 10 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 10 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 10 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 10 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 10 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 11 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 11 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 11 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 11 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 11 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 11 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 11 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 11 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 11 | 8 | 9937 | 28500 | 34.87%
[29 empty] | 2020 | February | 11 | 9 | 20487.5 | 28500 | 71.89%
[29 empty] | 2020 | February | 11 | 10 | 31351.5 | 28500 | 110%
[29 empty] | 2020 | February | 11 | 11 | 30064.5 | 28500 | 105.5%
[29 empty] | 2020 | February | 11 | 12 | 21633.5 | 28500 | 75.91%
[29 empty] | 2020 | February | 11 | 13 | 17288 | 28500 | 60.66%
[29 empty] | 2020 | February | 11 | 14 | 25464.5 | 28500 | 89.35%
[29 empty] | 2020 | February | 11 | 15 | 7011 | 28500 | 24.6%
[29 empty] | 2020 | February | 11 | 16 | 5943 | 28500 | 20.85%
[29 empty] | 2020 | February | 11 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 11 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 11 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 11 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 11 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 11 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 11 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 12 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 12 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 12 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 12 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 12 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 12 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 12 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 12 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 12 | 8 | 10500.5 | 28500 | 36.84%
[29 empty] | 2020 | February | 12 | 9 | 20896.5 | 28500 | 73.32%
[29 empty] | 2020 | February | 12 | 10 | 32153.5 | 28500 | 112.8%
[29 empty] | 2020 | February | 12 | 11 | 34465 | 28500 | 120.9%
[29 empty] | 2020 | February | 12 | 12 | 38669 | 28500 | 135.7%
[29 empty] | 2020 | February | 12 | 13 | 26268.5 | 28500 | 92.17%
[29 empty] | 2020 | February | 12 | 14 | 21856.5 | 28500 | 76.69%
[29 empty] | 2020 | February | 12 | 15 | 18688.5 | 28500 | 65.57%
[29 empty] | 2020 | February | 12 | 16 | 9438 | 28500 | 33.12%
[29 empty] | 2020 | February | 12 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 12 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 12 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 12 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 12 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 12 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 12 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 13 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 13 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 13 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 13 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 13 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 13 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 13 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 13 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 13 | 8 | 9545.5 | 28500 | 33.49%
[29 empty] | 2020 | February | 13 | 9 | 19943 | 28500 | 69.98%
[29 empty] | 2020 | February | 13 | 10 | 11028.5 | 28500 | 38.7%
[29 empty] | 2020 | February | 13 | 11 | 6938 | 28500 | 24.34%
[29 empty] | 2020 | February | 13 | 12 | 2335.5 | 28500 | 8.195%
[29 empty] | 2020 | February | 13 | 13 | 1193 | 28500 | 4.186%
[29 empty] | 2020 | February | 13 | 14 | 6771.5 | 28500 | 23.76%
[29 empty] | 2020 | February | 13 | 15 | 11587 | 28500 | 40.66%
[29 empty] | 2020 | February | 13 | 16 | 7976.5 | 28500 | 27.99%
[29 empty] | 2020 | February | 13 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 13 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 13 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 13 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 13 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 13 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 13 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 14 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 14 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 14 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 14 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 14 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 14 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 14 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 14 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 14 | 8 | 6906.5 | 28500 | 24.23%
[29 empty] | 2020 | February | 14 | 9 | 19568 | 28500 | 68.66%
[29 empty] | 2020 | February | 14 | 10 | 28694 | 28500 | 100.7%
[29 empty] | 2020 | February | 14 | 11 | 28431 | 28500 | 99.76%
[29 empty] | 2020 | February | 14 | 12 | 20408 | 28500 | 71.61%
[29 empty] | 2020 | February | 14 | 13 | 22774.5 | 28500 | 79.91%
[29 empty] | 2020 | February | 14 | 14 | 15791.5 | 28500 | 55.41%
[29 empty] | 2020 | February | 14 | 15 | 2471 | 28500 | 8.67%
[29 empty] | 2020 | February | 14 | 16 | 118.5 | 28500 | 0.4158%
[29 empty] | 2020 | February | 14 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 14 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 14 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 14 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 14 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 14 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 14 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 15 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 15 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 15 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 15 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 15 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 15 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 15 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 15 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 15 | 8 | 13 | 28500 | 0.04561%
[29 empty] | 2020 | February | 15 | 9 | 1750.5 | 28500 | 6.142%
[29 empty] | 2020 | February | 15 | 10 | 2688 | 28500 | 9.432%
[29 empty] | 2020 | February | 15 | 11 | 2571 | 28500 | 9.021%
[29 empty] | 2020 | February | 15 | 12 | 1930.5 | 28500 | 6.774%
[29 empty] | 2020 | February | 15 | 13 | 1241.5 | 28500 | 4.356%
[29 empty] | 2020 | February | 15 | 14 | 2873 | 28500 | 10.08%
[29 empty] | 2020 | February | 15 | 15 | 632.5 | 28500 | 2.219%
[29 empty] | 2020 | February | 15 | 16 | 665.5 | 28500 | 2.335%
[29 empty] | 2020 | February | 15 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 15 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 15 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 15 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 15 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 15 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 15 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 16 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 16 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 16 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 16 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 16 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 16 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 16 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 16 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 16 | 8 | 566 | 28500 | 1.986%
[29 empty] | 2020 | February | 16 | 9 | 1735 | 28500 | 6.088%
[29 empty] | 2020 | February | 16 | 10 | 1307.5 | 28500 | 4.588%
[29 empty] | 2020 | February | 16 | 11 | 2450.5 | 28500 | 8.598%
[29 empty] | 2020 | February | 16 | 12 | 1711.5 | 28500 | 6.005%
[29 empty] | 2020 | February | 16 | 13 | 3393.5 | 28500 | 11.91%
[29 empty] | 2020 | February | 16 | 14 | 1767.5 | 28500 | 6.202%
[29 empty] | 2020 | February | 16 | 15 | 1263.5 | 28500 | 4.433%
[29 empty] | 2020 | February | 16 | 16 | 251.5 | 28500 | 0.8825%
[29 empty] | 2020 | February | 16 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 16 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 16 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 16 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 16 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 16 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 16 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 17 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 17 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 17 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 17 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 17 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 17 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 17 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 17 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 17 | 8 | 9701 | 28500 | 34.04%
[29 empty] | 2020 | February | 17 | 9 | 22178 | 28500 | 77.82%
[29 empty] | 2020 | February | 17 | 10 | 30980.5 | 28500 | 108.7%
[29 empty] | 2020 | February | 17 | 11 | 33178.5 | 28500 | 116.4%
[29 empty] | 2020 | February | 17 | 12 | 16379 | 28500 | 57.47%
[29 empty] | 2020 | February | 17 | 13 | 4038.5 | 28500 | 14.17%
[29 empty] | 2020 | February | 17 | 14 | 8364.5 | 28500 | 29.35%
[29 empty] | 2020 | February | 17 | 15 | 3776.5 | 28500 | 13.25%
[29 empty] | 2020 | February | 17 | 16 | 11125.5 | 28500 | 39.04%
[29 empty] | 2020 | February | 17 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 17 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 17 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 17 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 17 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 17 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 17 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 18 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 18 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 18 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 18 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 18 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 18 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 18 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 18 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 18 | 8 | 8465.5 | 28500 | 29.7%
[29 empty] | 2020 | February | 18 | 9 | 20431 | 28500 | 71.69%
[29 empty] | 2020 | February | 18 | 10 | 30275.5 | 28500 | 106.2%
[29 empty] | 2020 | February | 18 | 11 | 27410.5 | 28500 | 96.18%
[29 empty] | 2020 | February | 18 | 12 | 17417.5 | 28500 | 61.11%
[29 empty] | 2020 | February | 18 | 13 | 34535.5 | 28500 | 121.2%
[29 empty] | 2020 | February | 18 | 14 | 8578 | 28500 | 30.1%
[29 empty] | 2020 | February | 18 | 15 | 9603 | 28500 | 33.69%
[29 empty] | 2020 | February | 18 | 16 | 1638.5 | 28500 | 5.749%
[29 empty] | 2020 | February | 18 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 18 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 18 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 18 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 18 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 18 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 18 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 19 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 19 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 19 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 19 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 19 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 19 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 19 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 19 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 19 | 8 | 6115.5 | 28500 | 21.46%
[29 empty] | 2020 | February | 19 | 9 | 6336 | 28500 | 22.23%
[29 empty] | 2020 | February | 19 | 10 | 7513.5 | 28500 | 26.36%
[29 empty] | 2020 | February | 19 | 11 | 7962 | 28500 | 27.94%
[29 empty] | 2020 | February | 19 | 12 | 3483 | 28500 | 12.22%
[29 empty] | 2020 | February | 19 | 13 | 8616.5 | 28500 | 30.23%
[29 empty] | 2020 | February | 19 | 14 | 5638.5 | 28500 | 19.78%
[29 empty] | 2020 | February | 19 | 15 | 1850 | 28500 | 6.491%
[29 empty] | 2020 | February | 19 | 16 | 517 | 28500 | 1.814%
[29 empty] | 2020 | February | 19 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 19 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 19 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 19 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 19 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 19 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 19 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 20 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 20 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 20 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 20 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 20 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 20 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 20 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 20 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 20 | 8 | 976.5 | 28500 | 3.426%
[29 empty] | 2020 | February | 20 | 9 | 3931.5 | 28500 | 13.79%
[29 empty] | 2020 | February | 20 | 10 | 1833.5 | 28500 | 6.433%
[29 empty] | 2020 | February | 20 | 11 | 2281.5 | 28500 | 8.005%
[29 empty] | 2020 | February | 20 | 12 | 7357 | 28500 | 25.81%
[29 empty] | 2020 | February | 20 | 13 | 1719.5 | 28500 | 6.033%
[29 empty] | 2020 | February | 20 | 14 | 1510.5 | 28500 | 5.3%
[29 empty] | 2020 | February | 20 | 15 | 2279.5 | 28500 | 7.998%
[29 empty] | 2020 | February | 20 | 16 | 6845 | 28500 | 24.02%
[29 empty] | 2020 | February | 20 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 20 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 20 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 20 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 20 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 20 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 20 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 21 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 21 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 21 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 21 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 21 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 21 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 21 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 21 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 21 | 8 | 2077.5 | 28500 | 7.289%
[29 empty] | 2020 | February | 21 | 9 | 8005 | 28500 | 28.09%
[29 empty] | 2020 | February | 21 | 10 | 14628 | 28500 | 51.33%
[29 empty] | 2020 | February | 21 | 11 | 17534 | 28500 | 61.52%
[29 empty] | 2020 | February | 21 | 12 | 8993 | 28500 | 31.55%
[29 empty] | 2020 | February | 21 | 13 | 9474 | 28500 | 33.24%
[29 empty] | 2020 | February | 21 | 14 | 6528.5 | 28500 | 22.91%
[29 empty] | 2020 | February | 21 | 15 | 7046 | 28500 | 24.72%
[29 empty] | 2020 | February | 21 | 16 | 4090.5 | 28500 | 14.35%
[29 empty] | 2020 | February | 21 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 21 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 21 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 21 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 21 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 21 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 21 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 22 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 22 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 22 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 22 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 22 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 22 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 22 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 22 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 22 | 8 | 1807 | 28500 | 6.34%
[29 empty] | 2020 | February | 22 | 9 | 5243.5 | 28500 | 18.4%
[29 empty] | 2020 | February | 22 | 10 | 3806.5 | 28500 | 13.36%
[29 empty] | 2020 | February | 22 | 11 | 8574 | 28500 | 30.08%
[29 empty] | 2020 | February | 22 | 12 | 24208.5 | 28500 | 84.94%
[29 empty] | 2020 | February | 22 | 13 | 23079.5 | 28500 | 80.98%
[29 empty] | 2020 | February | 22 | 14 | 8534.5 | 28500 | 29.95%
[29 empty] | 2020 | February | 22 | 15 | 1781 | 28500 | 6.249%
[29 empty] | 2020 | February | 22 | 16 | 1701 | 28500 | 5.968%
[29 empty] | 2020 | February | 22 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 22 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 22 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 22 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 22 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 22 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 22 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 23 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 23 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 23 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 23 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 23 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 23 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 23 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 23 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 23 | 8 | 538.5 | 28500 | 1.889%
[29 empty] | 2020 | February | 23 | 9 | 2149.5 | 28500 | 7.542%
[29 empty] | 2020 | February | 23 | 10 | 1994.5 | 28500 | 6.998%
[29 empty] | 2020 | February | 23 | 11 | 9344 | 28500 | 32.79%
[29 empty] | 2020 | February | 23 | 12 | 11421.5 | 28500 | 40.08%
[29 empty] | 2020 | February | 23 | 13 | 2891.5 | 28500 | 10.15%
[29 empty] | 2020 | February | 23 | 14 | 5619.5 | 28500 | 19.72%
[29 empty] | 2020 | February | 23 | 15 | 14426.5 | 28500 | 50.62%
[29 empty] | 2020 | February | 23 | 16 | 6872.5 | 28500 | 24.11%
[29 empty] | 2020 | February | 23 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 23 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 23 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 23 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 23 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 23 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 23 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 24 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 24 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 24 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 24 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 24 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 24 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 24 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 24 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 24 | 8 | 1146.5 | 28500 | 4.023%
[29 empty] | 2020 | February | 24 | 9 | 1945.5 | 28500 | 6.826%
[29 empty] | 2020 | February | 24 | 10 | 2434.5 | 28500 | 8.542%
[29 empty] | 2020 | February | 24 | 11 | 4623 | 28500 | 16.22%
[29 empty] | 2020 | February | 24 | 12 | 3364 | 28500 | 11.8%
[29 empty] | 2020 | February | 24 | 13 | 1467.5 | 28500 | 5.149%
[29 empty] | 2020 | February | 24 | 14 | 2244 | 28500 | 7.874%
[29 empty] | 2020 | February | 24 | 15 | 7380 | 28500 | 25.89%
[29 empty] | 2020 | February | 24 | 16 | 867 | 28500 | 3.042%
[29 empty] | 2020 | February | 24 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 24 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 24 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 24 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 24 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 24 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 24 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 25 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 25 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 25 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 25 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 25 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 25 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 25 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 25 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 25 | 8 | 13011 | 28500 | 45.65%
[29 empty] | 2020 | February | 25 | 9 | 21813 | 28500 | 76.54%
[29 empty] | 2020 | February | 25 | 10 | 13197.5 | 28500 | 46.31%
[29 empty] | 2020 | February | 25 | 11 | 26452.5 | 28500 | 92.82%
[29 empty] | 2020 | February | 25 | 12 | 19667 | 28500 | 69.01%
[29 empty] | 2020 | February | 25 | 13 | 17375 | 28500 | 60.96%
[29 empty] | 2020 | February | 25 | 14 | 7755.5 | 28500 | 27.21%
[29 empty] | 2020 | February | 25 | 15 | 11880.5 | 28500 | 41.69%
[29 empty] | 2020 | February | 25 | 16 | 2417.5 | 28500 | 8.482%
[29 empty] | 2020 | February | 25 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 25 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 25 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 25 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 25 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 25 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 25 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 26 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 26 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 26 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 26 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 26 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 26 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 26 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 26 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 26 | 8 | 14664 | 28500 | 51.45%
[29 empty] | 2020 | February | 26 | 9 | 26344.5 | 28500 | 92.44%
[29 empty] | 2020 | February | 26 | 10 | 25373 | 28500 | 89.03%
[29 empty] | 2020 | February | 26 | 11 | 14426 | 28500 | 50.62%
[29 empty] | 2020 | February | 26 | 12 | 2398 | 28500 | 8.414%
[29 empty] | 2020 | February | 26 | 13 | 24224 | 28500 | 85%
[29 empty] | 2020 | February | 26 | 14 | 15392.5 | 28500 | 54.01%
[29 empty] | 2020 | February | 26 | 15 | 10858 | 28500 | 38.1%
[29 empty] | 2020 | February | 26 | 16 | 11131 | 28500 | 39.06%
[29 empty] | 2020 | February | 26 | 17 | 189 | 28500 | 0.6632%
[29 empty] | 2020 | February | 26 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 26 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 26 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 26 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 26 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 26 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 27 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 27 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 27 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 27 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 27 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 27 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 27 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 27 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 27 | 8 | 4070 | 28500 | 14.28%
[29 empty] | 2020 | February | 27 | 9 | 2799 | 28500 | 9.821%
[29 empty] | 2020 | February | 27 | 10 | 5720 | 28500 | 20.07%
[29 empty] | 2020 | February | 27 | 11 | 10385.5 | 28500 | 36.44%
[29 empty] | 2020 | February | 27 | 12 | 1290 | 28500 | 4.526%
[29 empty] | 2020 | February | 27 | 13 | 10378 | 28500 | 36.41%
[29 empty] | 2020 | February | 27 | 14 | 3342.5 | 28500 | 11.73%
[29 empty] | 2020 | February | 27 | 15 | 16259.5 | 28500 | 57.05%
[29 empty] | 2020 | February | 27 | 16 | 13762.5 | 28500 | 48.29%
[29 empty] | 2020 | February | 27 | 17 | 205 | 28500 | 0.7193%
[29 empty] | 2020 | February | 27 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 27 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 27 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 27 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 27 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 27 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 28 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 28 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 28 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 28 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 28 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 28 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 28 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 28 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 28 | 8 | 2103.5 | 28500 | 7.381%
[29 empty] | 2020 | February | 28 | 9 | 1795 | 28500 | 6.298%
[29 empty] | 2020 | February | 28 | 10 | 2407.5 | 28500 | 8.447%
[29 empty] | 2020 | February | 28 | 11 | 2602.5 | 28500 | 9.132%
[29 empty] | 2020 | February | 28 | 12 | 5403.5 | 28500 | 18.96%
[29 empty] | 2020 | February | 28 | 13 | 5435.5 | 28500 | 19.07%
[29 empty] | 2020 | February | 28 | 14 | 2084.5 | 28500 | 7.314%
[29 empty] | 2020 | February | 28 | 15 | 1296.5 | 28500 | 4.549%
[29 empty] | 2020 | February | 28 | 16 | 1504.5 | 28500 | 5.279%
[29 empty] | 2020 | February | 28 | 17 | 13.5 | 28500 | 0.04737%
[29 empty] | 2020 | February | 28 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 28 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 28 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 28 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 28 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 28 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 29 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 29 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 29 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 29 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 29 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 29 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 29 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 29 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 29 | 8 | 1013 | 28500 | 3.554%
[29 empty] | 2020 | February | 29 | 9 | 2119.5 | 28500 | 7.437%
[29 empty] | 2020 | February | 29 | 10 | 6919 | 28500 | 24.28%
[29 empty] | 2020 | February | 29 | 11 | 2753.5 | 28500 | 9.661%
[29 empty] | 2020 | February | 29 | 12 | 40030.5 | 28500 | 140.5%
[29 empty] | 2020 | February | 29 | 13 | 31722 | 28500 | 111.3%
[29 empty] | 2020 | February | 29 | 14 | 33770.5 | 28500 | 118.5%
[29 empty] | 2020 | February | 29 | 15 | 24201 | 28500 | 84.92%
[29 empty] | 2020 | February | 29 | 16 | 198 | 28500 | 0.6947%
[29 empty] | 2020 | February | 29 | 17 | 490 | 28500 | 1.719%
[29 empty] | 2020 | February | 29 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 29 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 29 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 29 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 29 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | February | 29 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 1 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 1 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 1 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 1 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 1 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 1 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 1 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 1 | 7 | 460 | 28500 | 1.614%
[29 empty] | 2020 | March | 1 | 8 | 14329.5 | 28500 | 50.28%
[29 empty] | 2020 | March | 1 | 9 | 26823.5 | 28500 | 94.12%
[29 empty] | 2020 | March | 1 | 10 | 31579 | 28500 | 110.8%
[29 empty] | 2020 | March | 1 | 11 | 17936.5 | 28500 | 62.94%
[29 empty] | 2020 | March | 1 | 12 | 14331 | 28500 | 50.28%
[29 empty] | 2020 | March | 1 | 13 | 33829 | 28500 | 118.7%
[29 empty] | 2020 | March | 1 | 14 | 28004 | 28500 | 98.26%
[29 empty] | 2020 | March | 1 | 15 | 25338 | 28500 | 88.91%
[29 empty] | 2020 | March | 1 | 16 | 11830.5 | 28500 | 41.51%
[29 empty] | 2020 | March | 1 | 17 | 531.5 | 28500 | 1.865%
[29 empty] | 2020 | March | 1 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 1 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 1 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 1 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 1 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 1 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 2 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 2 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 2 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 2 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 2 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 2 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 2 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 2 | 7 | 174 | 28500 | 0.6105%
[29 empty] | 2020 | March | 2 | 8 | 13106.5 | 28500 | 45.99%
[29 empty] | 2020 | March | 2 | 9 | 6892.5 | 28500 | 24.18%
[29 empty] | 2020 | March | 2 | 10 | 6647.5 | 28500 | 23.32%
[29 empty] | 2020 | March | 2 | 11 | 26961 | 28500 | 94.6%
[29 empty] | 2020 | March | 2 | 12 | 9508.5 | 28500 | 33.36%
[29 empty] | 2020 | March | 2 | 13 | 25952.5 | 28500 | 91.06%
[29 empty] | 2020 | March | 2 | 14 | 31339 | 28500 | 110%
[29 empty] | 2020 | March | 2 | 15 | 14752.5 | 28500 | 51.76%
[29 empty] | 2020 | March | 2 | 16 | 11128.5 | 28500 | 39.05%
[29 empty] | 2020 | March | 2 | 17 | 516 | 28500 | 1.811%
[29 empty] | 2020 | March | 2 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 2 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 2 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 2 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 2 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 2 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 3 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 3 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 3 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 3 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 3 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 3 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 3 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 3 | 7 | 669.5 | 28500 | 2.349%
[29 empty] | 2020 | March | 3 | 8 | 14383.5 | 28500 | 50.47%
[29 empty] | 2020 | March | 3 | 9 | 27139.5 | 28500 | 95.23%
[29 empty] | 2020 | March | 3 | 10 | 27536 | 28500 | 96.62%
[29 empty] | 2020 | March | 3 | 11 | 19795.5 | 28500 | 69.46%
[29 empty] | 2020 | March | 3 | 12 | 2718 | 28500 | 9.537%
[29 empty] | 2020 | March | 3 | 13 | 3564.5 | 28500 | 12.51%
[29 empty] | 2020 | March | 3 | 14 | 4428 | 28500 | 15.54%
[29 empty] | 2020 | March | 3 | 15 | 3175.5 | 28500 | 11.14%
[29 empty] | 2020 | March | 3 | 16 | 9538 | 28500 | 33.47%
[29 empty] | 2020 | March | 3 | 17 | 121 | 28500 | 0.4246%
[29 empty] | 2020 | March | 3 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 3 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 3 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 3 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 3 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 3 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 4 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 4 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 4 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 4 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 4 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 4 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 4 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 4 | 7 | 178 | 28500 | 0.6246%
[29 empty] | 2020 | March | 4 | 8 | 3857 | 28500 | 13.53%
[29 empty] | 2020 | March | 4 | 9 | 6292 | 28500 | 22.08%
[29 empty] | 2020 | March | 4 | 10 | 7228.5 | 28500 | 25.36%
[29 empty] | 2020 | March | 4 | 11 | 15355 | 28500 | 53.88%
[29 empty] | 2020 | March | 4 | 12 | 16387 | 28500 | 57.5%
[29 empty] | 2020 | March | 4 | 13 | 10158.5 | 28500 | 35.64%
[29 empty] | 2020 | March | 4 | 14 | 2908.5 | 28500 | 10.21%
[29 empty] | 2020 | March | 4 | 15 | 2718.5 | 28500 | 9.539%
[29 empty] | 2020 | March | 4 | 16 | 4525.5 | 28500 | 15.88%
[29 empty] | 2020 | March | 4 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 4 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 4 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 4 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 4 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 4 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 4 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 5 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 5 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 5 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 5 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 5 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 5 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 5 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 5 | 7 | 75.5 | 28500 | 0.2649%
[29 empty] | 2020 | March | 5 | 8 | 430 | 28500 | 1.509%
[29 empty] | 2020 | March | 5 | 9 | 619.5 | 28500 | 2.174%
[29 empty] | 2020 | March | 5 | 10 | 1752.5 | 28500 | 6.149%
[29 empty] | 2020 | March | 5 | 11 | 2592.5 | 28500 | 9.096%
[29 empty] | 2020 | March | 5 | 12 | 3140 | 28500 | 11.02%
[29 empty] | 2020 | March | 5 | 13 | 1346.5 | 28500 | 4.725%
[29 empty] | 2020 | March | 5 | 14 | 3694 | 28500 | 12.96%
[29 empty] | 2020 | March | 5 | 15 | 1867 | 28500 | 6.551%
[29 empty] | 2020 | March | 5 | 16 | 854.5 | 28500 | 2.998%
[29 empty] | 2020 | March | 5 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 5 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 5 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 5 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 5 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 5 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 5 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 6 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 6 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 6 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 6 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 6 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 6 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 6 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 6 | 7 | 1188 | 28500 | 4.168%
[29 empty] | 2020 | March | 6 | 8 | 16169 | 28500 | 56.73%
[29 empty] | 2020 | March | 6 | 9 | 25015.5 | 28500 | 87.77%
[29 empty] | 2020 | March | 6 | 10 | 24659 | 28500 | 86.52%
[29 empty] | 2020 | March | 6 | 11 | 35768.5 | 28500 | 125.5%
[29 empty] | 2020 | March | 6 | 12 | 33913.5 | 28500 | 119%
[29 empty] | 2020 | March | 6 | 13 | 35851 | 28500 | 125.8%
[29 empty] | 2020 | March | 6 | 14 | 29859 | 28500 | 104.8%
[29 empty] | 2020 | March | 6 | 15 | 26694 | 28500 | 93.66%
[29 empty] | 2020 | March | 6 | 16 | 14511.5 | 28500 | 50.92%
[29 empty] | 2020 | March | 6 | 17 | 821.5 | 28500 | 2.882%
[29 empty] | 2020 | March | 6 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 6 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 6 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 6 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 6 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 6 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 7 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 7 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 7 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 7 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 7 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 7 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 7 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 7 | 7 | 553 | 28500 | 1.94%
[29 empty] | 2020 | March | 7 | 8 | 3093 | 28500 | 10.85%
[29 empty] | 2020 | March | 7 | 9 | 5272 | 28500 | 18.5%
[29 empty] | 2020 | March | 7 | 10 | 8471.5 | 28500 | 29.72%
[29 empty] | 2020 | March | 7 | 11 | 13603 | 28500 | 47.73%
[29 empty] | 2020 | March | 7 | 12 | 11384.5 | 28500 | 39.95%
[29 empty] | 2020 | March | 7 | 13 | 20945.5 | 28500 | 73.49%
[29 empty] | 2020 | March | 7 | 14 | 14735 | 28500 | 51.7%
[29 empty] | 2020 | March | 7 | 15 | 13230 | 28500 | 46.42%
[29 empty] | 2020 | March | 7 | 16 | 4386.5 | 28500 | 15.39%
[29 empty] | 2020 | March | 7 | 17 | 1243.5 | 28500 | 4.363%
[29 empty] | 2020 | March | 7 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 7 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 7 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 7 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 7 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 7 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 8 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 8 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 8 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 8 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 8 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 8 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 8 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 8 | 7 | 1171 | 28500 | 4.109%
[29 empty] | 2020 | March | 8 | 8 | 14084 | 28500 | 49.42%
[29 empty] | 2020 | March | 8 | 9 | 4564.5 | 28500 | 16.02%
[29 empty] | 2020 | March | 8 | 10 | 23493 | 28500 | 82.43%
[29 empty] | 2020 | March | 8 | 11 | 27454.5 | 28500 | 96.33%
[29 empty] | 2020 | March | 8 | 12 | 12367.5 | 28500 | 43.39%
[29 empty] | 2020 | March | 8 | 13 | 6399 | 28500 | 22.45%
[29 empty] | 2020 | March | 8 | 14 | 11456.5 | 28500 | 40.2%
[29 empty] | 2020 | March | 8 | 15 | 22566 | 28500 | 79.18%
[29 empty] | 2020 | March | 8 | 16 | 6939 | 28500 | 24.35%
[29 empty] | 2020 | March | 8 | 17 | 3469.5 | 28500 | 12.17%
[29 empty] | 2020 | March | 8 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 8 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 8 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 8 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 8 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 8 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 9 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 9 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 9 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 9 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 9 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 9 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 9 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 9 | 7 | 4169.5 | 28500 | 14.63%
[29 empty] | 2020 | March | 9 | 8 | 16956 | 28500 | 59.49%
[29 empty] | 2020 | March | 9 | 9 | 27526.5 | 28500 | 96.58%
[29 empty] | 2020 | March | 9 | 10 | 28548 | 28500 | 100.2%
[29 empty] | 2020 | March | 9 | 11 | 5902 | 28500 | 20.71%
[29 empty] | 2020 | March | 9 | 12 | 20421 | 28500 | 71.65%
[29 empty] | 2020 | March | 9 | 13 | 17292.5 | 28500 | 60.68%
[29 empty] | 2020 | March | 9 | 14 | 15792.5 | 28500 | 55.41%
[29 empty] | 2020 | March | 9 | 15 | 8355 | 28500 | 29.32%
[29 empty] | 2020 | March | 9 | 16 | 1291 | 28500 | 4.53%
[29 empty] | 2020 | March | 9 | 17 | 657 | 28500 | 2.305%
[29 empty] | 2020 | March | 9 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 9 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 9 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 9 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 9 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 9 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 10 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 10 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 10 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 10 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 10 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 10 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 10 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 10 | 7 | 1013.5 | 28500 | 3.556%
[29 empty] | 2020 | March | 10 | 8 | 3446.5 | 28500 | 12.09%
[29 empty] | 2020 | March | 10 | 9 | 5137.5 | 28500 | 18.03%
[29 empty] | 2020 | March | 10 | 10 | 8248 | 28500 | 28.94%
[29 empty] | 2020 | March | 10 | 11 | 7118.5 | 28500 | 24.98%
[29 empty] | 2020 | March | 10 | 12 | 5730 | 28500 | 20.11%
[29 empty] | 2020 | March | 10 | 13 | 8380 | 28500 | 29.4%
[29 empty] | 2020 | March | 10 | 14 | 10855 | 28500 | 38.09%
[29 empty] | 2020 | March | 10 | 15 | 3134 | 28500 | 11%
[29 empty] | 2020 | March | 10 | 16 | 4153.5 | 28500 | 14.57%
[29 empty] | 2020 | March | 10 | 17 | 324 | 28500 | 1.137%
[29 empty] | 2020 | March | 10 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 10 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 10 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 10 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 10 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 10 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 11 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 11 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 11 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 11 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 11 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 11 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 11 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 11 | 7 | 1241.5 | 28500 | 4.356%
[29 empty] | 2020 | March | 11 | 8 | 4502.5 | 28500 | 15.8%
[29 empty] | 2020 | March | 11 | 9 | 6426.5 | 28500 | 22.55%
[29 empty] | 2020 | March | 11 | 10 | 6467.5 | 28500 | 22.69%
[29 empty] | 2020 | March | 11 | 11 | 37293.5 | 28500 | 130.9%
[29 empty] | 2020 | March | 11 | 12 | 33373 | 28500 | 117.1%
[29 empty] | 2020 | March | 11 | 13 | 38030 | 28500 | 133.4%
[29 empty] | 2020 | March | 11 | 14 | 24680 | 28500 | 86.6%
[29 empty] | 2020 | March | 11 | 15 | 26593.5 | 28500 | 93.31%
[29 empty] | 2020 | March | 11 | 16 | 15298.5 | 28500 | 53.68%
[29 empty] | 2020 | March | 11 | 17 | 4129.5 | 28500 | 14.49%
[29 empty] | 2020 | March | 11 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 11 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 11 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 11 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 11 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 11 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 12 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 12 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 12 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 12 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 12 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 12 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 12 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 12 | 7 | 5309 | 28500 | 18.63%
[29 empty] | 2020 | March | 12 | 8 | 18048.5 | 28500 | 63.33%
[29 empty] | 2020 | March | 12 | 9 | 27809.5 | 28500 | 97.58%
[29 empty] | 2020 | March | 12 | 10 | 12200.5 | 28500 | 42.81%
[29 empty] | 2020 | March | 12 | 11 | 34860.5 | 28500 | 122.3%
[29 empty] | 2020 | March | 12 | 12 | 31899.5 | 28500 | 111.9%
[29 empty] | 2020 | March | 12 | 13 | 38153 | 28500 | 133.9%
[29 empty] | 2020 | March | 12 | 14 | 9657.5 | 28500 | 33.89%
[29 empty] | 2020 | March | 12 | 15 | 18220 | 28500 | 63.93%
[29 empty] | 2020 | March | 12 | 16 | 9188 | 28500 | 32.24%
[29 empty] | 2020 | March | 12 | 17 | 4805.5 | 28500 | 16.86%
[29 empty] | 2020 | March | 12 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 12 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 12 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 12 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 12 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 12 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 13 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 13 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 13 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 13 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 13 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 13 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 13 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 13 | 7 | 4891 | 28500 | 17.16%
[29 empty] | 2020 | March | 13 | 8 | 17498.5 | 28500 | 61.4%
[29 empty] | 2020 | March | 13 | 9 | 8365.5 | 28500 | 29.35%
[29 empty] | 2020 | March | 13 | 10 | 4245 | 28500 | 14.89%
[29 empty] | 2020 | March | 13 | 11 | 6789.5 | 28500 | 23.82%
[29 empty] | 2020 | March | 13 | 12 | 18789 | 28500 | 65.93%
[29 empty] | 2020 | March | 13 | 13 | 27373 | 28500 | 96.05%
[29 empty] | 2020 | March | 13 | 14 | 19580 | 28500 | 68.7%
[29 empty] | 2020 | March | 13 | 15 | 24468 | 28500 | 85.85%
[29 empty] | 2020 | March | 13 | 16 | 8771 | 28500 | 30.78%
[29 empty] | 2020 | March | 13 | 17 | 4346 | 28500 | 15.25%
[29 empty] | 2020 | March | 13 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 13 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 13 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 13 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 13 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 13 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 14 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 14 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 14 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 14 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 14 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 14 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 14 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 14 | 7 | 1743 | 28500 | 6.116%
[29 empty] | 2020 | March | 14 | 8 | 2154.5 | 28500 | 7.56%
[29 empty] | 2020 | March | 14 | 9 | 10713 | 28500 | 37.59%
[29 empty] | 2020 | March | 14 | 10 | 28019 | 28500 | 98.31%
[29 empty] | 2020 | March | 14 | 11 | 18709.5 | 28500 | 65.65%
[29 empty] | 2020 | March | 14 | 12 | 12782.5 | 28500 | 44.85%
[29 empty] | 2020 | March | 14 | 13 | 13334 | 28500 | 46.79%
[29 empty] | 2020 | March | 14 | 14 | 6722 | 28500 | 23.59%
[29 empty] | 2020 | March | 14 | 15 | 7121 | 28500 | 24.99%
[29 empty] | 2020 | March | 14 | 16 | 6200 | 28500 | 21.75%
[29 empty] | 2020 | March | 14 | 17 | 832.5 | 28500 | 2.921%
[29 empty] | 2020 | March | 14 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 14 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 14 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 14 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 14 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 14 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 15 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 15 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 15 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 15 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 15 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 15 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 15 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 15 | 7 | 5767 | 28500 | 20.24%
[29 empty] | 2020 | March | 15 | 8 | 5303 | 28500 | 18.61%
[29 empty] | 2020 | March | 15 | 9 | 4114 | 28500 | 14.44%
[29 empty] | 2020 | March | 15 | 10 | 6888.5 | 28500 | 24.17%
[29 empty] | 2020 | March | 15 | 11 | 14691.5 | 28500 | 51.55%
[29 empty] | 2020 | March | 15 | 12 | 3003.5 | 28500 | 10.54%
[29 empty] | 2020 | March | 15 | 13 | 4485 | 28500 | 15.74%
[29 empty] | 2020 | March | 15 | 14 | 2235 | 28500 | 7.842%
[29 empty] | 2020 | March | 15 | 15 | 3816.5 | 28500 | 13.39%
[29 empty] | 2020 | March | 15 | 16 | 5971.5 | 28500 | 20.95%
[29 empty] | 2020 | March | 15 | 17 | 2321.5 | 28500 | 8.146%
[29 empty] | 2020 | March | 15 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 15 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 15 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 15 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 15 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 15 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 16 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 16 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 16 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 16 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 16 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 16 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 16 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 16 | 7 | 6644.5 | 28500 | 23.31%
[29 empty] | 2020 | March | 16 | 8 | 18965.5 | 28500 | 66.55%
[29 empty] | 2020 | March | 16 | 9 | 29556.5 | 28500 | 103.7%
[29 empty] | 2020 | March | 16 | 10 | 33136.5 | 28500 | 116.3%
[29 empty] | 2020 | March | 16 | 11 | 31127.5 | 28500 | 109.2%
[29 empty] | 2020 | March | 16 | 12 | 41346 | 28500 | 145.1%
[29 empty] | 2020 | March | 16 | 13 | 38992.5 | 28500 | 136.8%
[29 empty] | 2020 | March | 16 | 14 | 35904.5 | 28500 | 126%
[29 empty] | 2020 | March | 16 | 15 | 28459 | 28500 | 99.86%
[29 empty] | 2020 | March | 16 | 16 | 16527.5 | 28500 | 57.99%
[29 empty] | 2020 | March | 16 | 17 | 5553 | 28500 | 19.48%
[29 empty] | 2020 | March | 16 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 16 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 16 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 16 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 16 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 16 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 17 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 17 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 17 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 17 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 17 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 17 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 17 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 17 | 7 | 5562 | 28500 | 19.52%
[29 empty] | 2020 | March | 17 | 8 | 7184.5 | 28500 | 25.21%
[29 empty] | 2020 | March | 17 | 9 | 28104 | 28500 | 98.61%
[29 empty] | 2020 | March | 17 | 10 | 33247 | 28500 | 116.7%
[29 empty] | 2020 | March | 17 | 11 | 23366.5 | 28500 | 81.99%
[29 empty] | 2020 | March | 17 | 12 | 24630 | 28500 | 86.42%
[29 empty] | 2020 | March | 17 | 13 | 24694 | 28500 | 86.65%
[29 empty] | 2020 | March | 17 | 14 | 10724 | 28500 | 37.63%
[29 empty] | 2020 | March | 17 | 15 | 8949 | 28500 | 31.4%
[29 empty] | 2020 | March | 17 | 16 | 5128.5 | 28500 | 17.99%
[29 empty] | 2020 | March | 17 | 17 | 1438.5 | 28500 | 5.047%
[29 empty] | 2020 | March | 17 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 17 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 17 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 17 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 17 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 17 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 18 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 18 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 18 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 18 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 18 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 18 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 18 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 18 | 7 | 482.5 | 28500 | 1.693%
[29 empty] | 2020 | March | 18 | 8 | 1427.5 | 28500 | 5.009%
[29 empty] | 2020 | March | 18 | 9 | 4641 | 28500 | 16.28%
[29 empty] | 2020 | March | 18 | 10 | 6212 | 28500 | 21.8%
[29 empty] | 2020 | March | 18 | 11 | 14819.5 | 28500 | 52%
[29 empty] | 2020 | March | 18 | 12 | 12590 | 28500 | 44.18%
[29 empty] | 2020 | March | 18 | 13 | 17446.5 | 28500 | 61.22%
[29 empty] | 2020 | March | 18 | 14 | 21432 | 28500 | 75.2%
[29 empty] | 2020 | March | 18 | 15 | 11397 | 28500 | 39.99%
[29 empty] | 2020 | March | 18 | 16 | 13860 | 28500 | 48.63%
[29 empty] | 2020 | March | 18 | 17 | 3168.5 | 28500 | 11.12%
[29 empty] | 2020 | March | 18 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 18 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 18 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 18 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 18 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 18 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 19 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 19 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 19 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 19 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 19 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 19 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 19 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 19 | 7 | 1126 | 28500 | 3.951%
[29 empty] | 2020 | March | 19 | 8 | 2119.5 | 28500 | 7.437%
[29 empty] | 2020 | March | 19 | 9 | 1019.5 | 28500 | 3.577%
[29 empty] | 2020 | March | 19 | 10 | 1229 | 28500 | 4.312%
[29 empty] | 2020 | March | 19 | 11 | 1478.5 | 28500 | 5.188%
[29 empty] | 2020 | March | 19 | 12 | 2105 | 28500 | 7.386%
[29 empty] | 2020 | March | 19 | 13 | 1841.5 | 28500 | 6.461%
[29 empty] | 2020 | March | 19 | 14 | 2065.5 | 28500 | 7.247%
[29 empty] | 2020 | March | 19 | 15 | 1585.5 | 28500 | 5.563%
[29 empty] | 2020 | March | 19 | 16 | 4187 | 28500 | 14.69%
[29 empty] | 2020 | March | 19 | 17 | 1183.5 | 28500 | 4.153%
[29 empty] | 2020 | March | 19 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 19 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 19 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 19 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 19 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 19 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 20 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 20 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 20 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 20 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 20 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 20 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 20 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 20 | 7 | 1983 | 28500 | 6.958%
[29 empty] | 2020 | March | 20 | 8 | 10781.5 | 28500 | 37.83%
[29 empty] | 2020 | March | 20 | 9 | 10098 | 28500 | 35.43%
[29 empty] | 2020 | March | 20 | 10 | 11535.5 | 28500 | 40.48%
[29 empty] | 2020 | March | 20 | 11 | 13647.5 | 28500 | 47.89%
[29 empty] | 2020 | March | 20 | 12 | 16748 | 28500 | 58.76%
[29 empty] | 2020 | March | 20 | 13 | 17419.5 | 28500 | 61.12%
[29 empty] | 2020 | March | 20 | 14 | 5450 | 28500 | 19.12%
[29 empty] | 2020 | March | 20 | 15 | 6201 | 28500 | 21.76%
[29 empty] | 2020 | March | 20 | 16 | 8621 | 28500 | 30.25%
[29 empty] | 2020 | March | 20 | 17 | 2946.5 | 28500 | 10.34%
[29 empty] | 2020 | March | 20 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 20 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 20 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 20 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 20 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 20 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 21 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 21 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 21 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 21 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 21 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 21 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 21 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 21 | 7 | 5786 | 28500 | 20.3%
[29 empty] | 2020 | March | 21 | 8 | 13165.5 | 28500 | 46.19%
[29 empty] | 2020 | March | 21 | 9 | 25355 | 28500 | 88.96%
[29 empty] | 2020 | March | 21 | 10 | 40750.5 | 28500 | 143%
[29 empty] | 2020 | March | 21 | 11 | 45461.5 | 28500 | 159.5%
[29 empty] | 2020 | March | 21 | 12 | 45154.5 | 28500 | 158.4%
[29 empty] | 2020 | March | 21 | 13 | 45209 | 28500 | 158.6%
[29 empty] | 2020 | March | 21 | 14 | 35279 | 28500 | 123.8%
[29 empty] | 2020 | March | 21 | 15 | 29452.5 | 28500 | 103.3%
[29 empty] | 2020 | March | 21 | 16 | 11221 | 28500 | 39.37%
[29 empty] | 2020 | March | 21 | 17 | 3455.5 | 28500 | 12.12%
[29 empty] | 2020 | March | 21 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 21 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 21 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 21 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 21 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 21 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 22 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 22 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 22 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 22 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 22 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 22 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 22 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 22 | 7 | 4934.5 | 28500 | 17.31%
[29 empty] | 2020 | March | 22 | 8 | 14071.5 | 28500 | 49.37%
[29 empty] | 2020 | March | 22 | 9 | 30605.5 | 28500 | 107.4%
[29 empty] | 2020 | March | 22 | 10 | 33475.5 | 28500 | 117.5%
[29 empty] | 2020 | March | 22 | 11 | 45512.5 | 28500 | 159.7%
[29 empty] | 2020 | March | 22 | 12 | 46795 | 28500 | 164.2%
[29 empty] | 2020 | March | 22 | 13 | 44854 | 28500 | 157.4%
[29 empty] | 2020 | March | 22 | 14 | 39511 | 28500 | 138.6%
[29 empty] | 2020 | March | 22 | 15 | 29568 | 28500 | 103.7%
[29 empty] | 2020 | March | 22 | 16 | 18772.5 | 28500 | 65.87%
[29 empty] | 2020 | March | 22 | 17 | 6379 | 28500 | 22.38%
[29 empty] | 2020 | March | 22 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 22 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 22 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 22 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 22 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 22 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 23 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 23 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 23 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 23 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 23 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 23 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 23 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 23 | 7 | 8893 | 28500 | 31.2%
[29 empty] | 2020 | March | 23 | 8 | 21786 | 28500 | 76.44%
[29 empty] | 2020 | March | 23 | 9 | 32291 | 28500 | 113.3%
[29 empty] | 2020 | March | 23 | 10 | 39119.5 | 28500 | 137.3%
[29 empty] | 2020 | March | 23 | 11 | 44609.5 | 28500 | 156.5%
[29 empty] | 2020 | March | 23 | 12 | 46053 | 28500 | 161.6%
[29 empty] | 2020 | March | 23 | 13 | 41907.5 | 28500 | 147%
[29 empty] | 2020 | March | 23 | 14 | 37532.5 | 28500 | 131.7%
[29 empty] | 2020 | March | 23 | 15 | 29256.5 | 28500 | 102.7%
[29 empty] | 2020 | March | 23 | 16 | 18682 | 28500 | 65.55%
[29 empty] | 2020 | March | 23 | 17 | 6491.5 | 28500 | 22.78%
[29 empty] | 2020 | March | 23 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 23 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 23 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 23 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 23 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 23 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 24 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 24 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 24 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 24 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 24 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 24 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 24 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 24 | 7 | 8767.5 | 28500 | 30.76%
[29 empty] | 2020 | March | 24 | 8 | 20772 | 28500 | 72.88%
[29 empty] | 2020 | March | 24 | 9 | 31238 | 28500 | 109.6%
[29 empty] | 2020 | March | 24 | 10 | 38328 | 28500 | 134.5%
[29 empty] | 2020 | March | 24 | 11 | 43278.5 | 28500 | 151.9%
[29 empty] | 2020 | March | 24 | 12 | 44741.5 | 28500 | 157%
[29 empty] | 2020 | March | 24 | 13 | 41484 | 28500 | 145.6%
[29 empty] | 2020 | March | 24 | 14 | 37334.5 | 28500 | 131%
[29 empty] | 2020 | March | 24 | 15 | 28743.5 | 28500 | 100.9%
[29 empty] | 2020 | March | 24 | 16 | 18413.5 | 28500 | 64.61%
[29 empty] | 2020 | March | 24 | 17 | 6090 | 28500 | 21.37%
[29 empty] | 2020 | March | 24 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 24 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 24 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 24 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 24 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 24 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 25 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 25 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 25 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 25 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 25 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 25 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 25 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 25 | 7 | 8670.5 | 28500 | 30.42%
[29 empty] | 2020 | March | 25 | 8 | 21193.5 | 28500 | 74.36%
[29 empty] | 2020 | March | 25 | 9 | 31169.5 | 28500 | 109.4%
[29 empty] | 2020 | March | 25 | 10 | 37698 | 28500 | 132.3%
[29 empty] | 2020 | March | 25 | 11 | 41704 | 28500 | 146.3%
[29 empty] | 2020 | March | 25 | 12 | 43715.5 | 28500 | 153.4%
[29 empty] | 2020 | March | 25 | 13 | 41187 | 28500 | 144.5%
[29 empty] | 2020 | March | 25 | 14 | 36819.5 | 28500 | 129.2%
[29 empty] | 2020 | March | 25 | 15 | 28648 | 28500 | 100.5%
[29 empty] | 2020 | March | 25 | 16 | 18342.5 | 28500 | 64.36%
[29 empty] | 2020 | March | 25 | 17 | 6475 | 28500 | 22.72%
[29 empty] | 2020 | March | 25 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 25 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 25 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 25 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 25 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 25 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 26 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 26 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 26 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 26 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 26 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 26 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 26 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 26 | 7 | 8147.5 | 28500 | 28.59%
[29 empty] | 2020 | March | 26 | 8 | 20604.5 | 28500 | 72.3%
[29 empty] | 2020 | March | 26 | 9 | 30729 | 28500 | 107.8%
[29 empty] | 2020 | March | 26 | 10 | 36980.5 | 28500 | 129.8%
[29 empty] | 2020 | March | 26 | 11 | 42488 | 28500 | 149.1%
[29 empty] | 2020 | March | 26 | 12 | 44929.5 | 28500 | 157.6%
[29 empty] | 2020 | March | 26 | 13 | 41853.5 | 28500 | 146.9%
[29 empty] | 2020 | March | 26 | 14 | 36860.5 | 28500 | 129.3%
[29 empty] | 2020 | March | 26 | 15 | 28488 | 28500 | 99.96%
[29 empty] | 2020 | March | 26 | 16 | 16591.5 | 28500 | 58.22%
[29 empty] | 2020 | March | 26 | 17 | 6823.5 | 28500 | 23.94%
[29 empty] | 2020 | March | 26 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 26 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 26 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 26 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 26 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 26 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 27 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 27 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 27 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 27 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 27 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 27 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 27 | 6 | 101 | 28500 | 0.3544%
[29 empty] | 2020 | March | 27 | 7 | 8265 | 28500 | 29%
[29 empty] | 2020 | March | 27 | 8 | 20152.5 | 28500 | 70.71%
[29 empty] | 2020 | March | 27 | 9 | 30483 | 28500 | 107%
[29 empty] | 2020 | March | 27 | 10 | 37566 | 28500 | 131.8%
[29 empty] | 2020 | March | 27 | 11 | 42163.5 | 28500 | 147.9%
[29 empty] | 2020 | March | 27 | 12 | 43700.5 | 28500 | 153.3%
[29 empty] | 2020 | March | 27 | 13 | 41156 | 28500 | 144.4%
[29 empty] | 2020 | March | 27 | 14 | 36456.5 | 28500 | 127.9%
[29 empty] | 2020 | March | 27 | 15 | 28349 | 28500 | 99.47%
[29 empty] | 2020 | March | 27 | 16 | 17767.5 | 28500 | 62.34%
[29 empty] | 2020 | March | 27 | 17 | 6198 | 28500 | 21.75%
[29 empty] | 2020 | March | 27 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 27 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 27 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 27 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 27 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 27 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 28 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 28 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 28 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 28 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 28 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 28 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 28 | 6 | 149 | 28500 | 0.5228%
[29 empty] | 2020 | March | 28 | 7 | 7880.5 | 28500 | 27.65%
[29 empty] | 2020 | March | 28 | 8 | 19564.5 | 28500 | 68.65%
[29 empty] | 2020 | March | 28 | 9 | 29597.5 | 28500 | 103.9%
[29 empty] | 2020 | March | 28 | 10 | 37089 | 28500 | 130.1%
[29 empty] | 2020 | March | 28 | 11 | 41351.5 | 28500 | 145.1%
[29 empty] | 2020 | March | 28 | 12 | 41232 | 28500 | 144.7%
[29 empty] | 2020 | March | 28 | 13 | 10662 | 28500 | 37.41%
[29 empty] | 2020 | March | 28 | 14 | 6483 | 28500 | 22.75%
[29 empty] | 2020 | March | 28 | 15 | 9599.5 | 28500 | 33.68%
[29 empty] | 2020 | March | 28 | 16 | 9846.5 | 28500 | 34.55%
[29 empty] | 2020 | March | 28 | 17 | 3933 | 28500 | 13.8%
[29 empty] | 2020 | March | 28 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 28 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 28 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 28 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 28 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 28 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 29 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 29 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 29 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 29 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 29 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 29 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 29 | 6 | 101 | 28500 | 0.3544%
[29 empty] | 2020 | March | 29 | 7 | 9354 | 28500 | 32.82%
[29 empty] | 2020 | March | 29 | 8 | 13618.5 | 28500 | 47.78%
[29 empty] | 2020 | March | 29 | 9 | 23688 | 28500 | 83.12%
[29 empty] | 2020 | March | 29 | 10 | 39422 | 28500 | 138.3%
[29 empty] | 2020 | March | 29 | 11 | 25759 | 28500 | 90.38%
[29 empty] | 2020 | March | 29 | 12 | 19489 | 28500 | 68.38%
[29 empty] | 2020 | March | 29 | 13 | 39702.5 | 28500 | 139.3%
[29 empty] | 2020 | March | 29 | 14 | 4215 | 28500 | 14.79%
[29 empty] | 2020 | March | 29 | 15 | 9280.5 | 28500 | 32.56%
[29 empty] | 2020 | March | 29 | 16 | 16979 | 28500 | 59.58%
[29 empty] | 2020 | March | 29 | 17 | 4273.5 | 28500 | 14.99%
[29 empty] | 2020 | March | 29 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 29 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 29 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 29 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 29 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 29 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 30 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 30 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 30 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 30 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 30 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 30 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 30 | 6 | 101.5 | 28500 | 0.3561%
[29 empty] | 2020 | March | 30 | 7 | 4353.5 | 28500 | 15.28%
[29 empty] | 2020 | March | 30 | 8 | 6367 | 28500 | 22.34%
[29 empty] | 2020 | March | 30 | 9 | 5281.5 | 28500 | 18.53%
[29 empty] | 2020 | March | 30 | 10 | 8051.5 | 28500 | 28.25%
[29 empty] | 2020 | March | 30 | 11 | 4225.5 | 28500 | 14.83%
[29 empty] | 2020 | March | 30 | 12 | 5812 | 28500 | 20.39%
[29 empty] | 2020 | March | 30 | 13 | 3294 | 28500 | 11.56%
[29 empty] | 2020 | March | 30 | 14 | 3172 | 28500 | 11.13%
[29 empty] | 2020 | March | 30 | 15 | 17484.5 | 28500 | 61.35%
[29 empty] | 2020 | March | 30 | 16 | 9763.5 | 28500 | 34.26%
[29 empty] | 2020 | March | 30 | 17 | 3846.5 | 28500 | 13.5%
[29 empty] | 2020 | March | 30 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 30 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 30 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 30 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 30 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 30 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 31 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 31 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 31 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 31 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 31 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 31 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 31 | 6 | 374.5 | 28500 | 1.314%
[29 empty] | 2020 | March | 31 | 7 | 6370 | 28500 | 22.35%
[29 empty] | 2020 | March | 31 | 8 | 20226.5 | 28500 | 70.97%
[29 empty] | 2020 | March | 31 | 9 | 8680.5 | 28500 | 30.46%
[29 empty] | 2020 | March | 31 | 10 | 21767.5 | 28500 | 76.38%
[29 empty] | 2020 | March | 31 | 11 | 30364.5 | 28500 | 106.5%
[29 empty] | 2020 | March | 31 | 12 | 16418.5 | 28500 | 57.61%
[29 empty] | 2020 | March | 31 | 13 | 27232 | 28500 | 95.55%
[29 empty] | 2020 | March | 31 | 14 | 8008 | 28500 | 28.1%
[29 empty] | 2020 | March | 31 | 15 | 17423.5 | 28500 | 61.14%
[29 empty] | 2020 | March | 31 | 16 | 18349 | 28500 | 64.38%
[29 empty] | 2020 | March | 31 | 17 | 7015 | 28500 | 24.61%
[29 empty] | 2020 | March | 31 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 31 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 31 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 31 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 31 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | March | 31 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 1 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 1 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 1 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 1 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 1 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 1 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 1 | 6 | 604 | 28500 | 2.119%
[29 empty] | 2020 | April | 1 | 7 | 10041 | 28500 | 35.23%
[29 empty] | 2020 | April | 1 | 8 | 21844.5 | 28500 | 76.65%
[29 empty] | 2020 | April | 1 | 9 | 30851 | 28500 | 108.2%
[29 empty] | 2020 | April | 1 | 10 | 37739.5 | 28500 | 132.4%
[29 empty] | 2020 | April | 1 | 11 | 34082 | 28500 | 119.6%
[29 empty] | 2020 | April | 1 | 12 | 8410.5 | 28500 | 29.51%
[29 empty] | 2020 | April | 1 | 13 | 5160 | 28500 | 18.11%
[29 empty] | 2020 | April | 1 | 14 | 3627 | 28500 | 12.73%
[29 empty] | 2020 | April | 1 | 15 | 3948.5 | 28500 | 13.85%
[29 empty] | 2020 | April | 1 | 16 | 3329.5 | 28500 | 11.68%
[29 empty] | 2020 | April | 1 | 17 | 2007.5 | 28500 | 7.044%
[29 empty] | 2020 | April | 1 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 1 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 1 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 1 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 1 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 1 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 2 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 2 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 2 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 2 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 2 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 2 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 2 | 6 | 285 | 28500 | 1%
[29 empty] | 2020 | April | 2 | 7 | 3494.5 | 28500 | 12.26%
[29 empty] | 2020 | April | 2 | 8 | 6474.5 | 28500 | 22.72%
[29 empty] | 2020 | April | 2 | 9 | 26635.5 | 28500 | 93.46%
[29 empty] | 2020 | April | 2 | 10 | 29970.5 | 28500 | 105.2%
[29 empty] | 2020 | April | 2 | 11 | 8845.5 | 28500 | 31.04%
[29 empty] | 2020 | April | 2 | 12 | 5787 | 28500 | 20.31%
[29 empty] | 2020 | April | 2 | 13 | 14480.5 | 28500 | 50.81%
[29 empty] | 2020 | April | 2 | 14 | 15370 | 28500 | 53.93%
[29 empty] | 2020 | April | 2 | 15 | 7652.5 | 28500 | 26.85%
[29 empty] | 2020 | April | 2 | 16 | 6230.5 | 28500 | 21.86%
[29 empty] | 2020 | April | 2 | 17 | 3976.5 | 28500 | 13.95%
[29 empty] | 2020 | April | 2 | 18 | 57.5 | 28500 | 0.2018%
[29 empty] | 2020 | April | 2 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 2 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 2 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 2 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 2 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 3 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 3 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 3 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 3 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 3 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 3 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 3 | 6 | 254 | 28500 | 0.8912%
[29 empty] | 2020 | April | 3 | 7 | 1745.5 | 28500 | 6.125%
[29 empty] | 2020 | April | 3 | 8 | 6136 | 28500 | 21.53%
[29 empty] | 2020 | April | 3 | 9 | 12928.5 | 28500 | 45.36%
[29 empty] | 2020 | April | 3 | 10 | 6060.5 | 28500 | 21.26%
[29 empty] | 2020 | April | 3 | 11 | 8503.5 | 28500 | 29.84%
[29 empty] | 2020 | April | 3 | 12 | 11488.5 | 28500 | 40.31%
[29 empty] | 2020 | April | 3 | 13 | 24649.5 | 28500 | 86.49%
[29 empty] | 2020 | April | 3 | 14 | 13432.5 | 28500 | 47.13%
[29 empty] | 2020 | April | 3 | 15 | 21587.5 | 28500 | 75.75%
[29 empty] | 2020 | April | 3 | 16 | 12166 | 28500 | 42.69%
[29 empty] | 2020 | April | 3 | 17 | 4909 | 28500 | 17.22%
[29 empty] | 2020 | April | 3 | 18 | 120 | 28500 | 0.4211%
[29 empty] | 2020 | April | 3 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 3 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 3 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 3 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 3 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 4 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 4 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 4 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 4 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 4 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 4 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 4 | 6 | 791 | 28500 | 2.775%
[29 empty] | 2020 | April | 4 | 7 | 6340 | 28500 | 22.25%
[29 empty] | 2020 | April | 4 | 8 | 18939.5 | 28500 | 66.45%
[29 empty] | 2020 | April | 4 | 9 | 29119 | 28500 | 102.2%
[29 empty] | 2020 | April | 4 | 10 | 37164 | 28500 | 130.4%
[29 empty] | 2020 | April | 4 | 11 | 41839 | 28500 | 146.8%
[29 empty] | 2020 | April | 4 | 12 | 43089 | 28500 | 151.2%
[29 empty] | 2020 | April | 4 | 13 | 40354.5 | 28500 | 141.6%
[29 empty] | 2020 | April | 4 | 14 | 36302 | 28500 | 127.4%
[29 empty] | 2020 | April | 4 | 15 | 28651 | 28500 | 100.5%
[29 empty] | 2020 | April | 4 | 16 | 18567.5 | 28500 | 65.15%
[29 empty] | 2020 | April | 4 | 17 | 6912.5 | 28500 | 24.25%
[29 empty] | 2020 | April | 4 | 18 | 165 | 28500 | 0.5789%
[29 empty] | 2020 | April | 4 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 4 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 4 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 4 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 4 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 5 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 5 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 5 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 5 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 5 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 5 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 5 | 6 | 1021.5 | 28500 | 3.584%
[29 empty] | 2020 | April | 5 | 7 | 10723.5 | 28500 | 37.63%
[29 empty] | 2020 | April | 5 | 8 | 22648 | 28500 | 79.47%
[29 empty] | 2020 | April | 5 | 9 | 32003 | 28500 | 112.3%
[29 empty] | 2020 | April | 5 | 10 | 38585 | 28500 | 135.4%
[29 empty] | 2020 | April | 5 | 11 | 42476 | 28500 | 149%
[29 empty] | 2020 | April | 5 | 12 | 43696 | 28500 | 153.3%
[29 empty] | 2020 | April | 5 | 13 | 41412.5 | 28500 | 145.3%
[29 empty] | 2020 | April | 5 | 14 | 35909.5 | 28500 | 126%
[29 empty] | 2020 | April | 5 | 15 | 28593.5 | 28500 | 100.3%
[29 empty] | 2020 | April | 5 | 16 | 18472 | 28500 | 64.81%
[29 empty] | 2020 | April | 5 | 17 | 7038 | 28500 | 24.69%
[29 empty] | 2020 | April | 5 | 18 | 254.5 | 28500 | 0.893%
[29 empty] | 2020 | April | 5 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 5 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 5 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 5 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 5 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 6 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 6 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 6 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 6 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 6 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 6 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 6 | 6 | 1032 | 28500 | 3.621%
[29 empty] | 2020 | April | 6 | 7 | 7228.5 | 28500 | 25.36%
[29 empty] | 2020 | April | 6 | 8 | 1775.5 | 28500 | 6.23%
[29 empty] | 2020 | April | 6 | 9 | 8548 | 28500 | 29.99%
[29 empty] | 2020 | April | 6 | 10 | 5089.5 | 28500 | 17.86%
[29 empty] | 2020 | April | 6 | 11 | 35709.5 | 28500 | 125.3%
[29 empty] | 2020 | April | 6 | 12 | 39333 | 28500 | 138%
[29 empty] | 2020 | April | 6 | 13 | 18404.5 | 28500 | 64.58%
[29 empty] | 2020 | April | 6 | 14 | 14407.5 | 28500 | 50.55%
[29 empty] | 2020 | April | 6 | 15 | 10243.5 | 28500 | 35.94%
[29 empty] | 2020 | April | 6 | 16 | 8215.5 | 28500 | 28.83%
[29 empty] | 2020 | April | 6 | 17 | 3599.5 | 28500 | 12.63%
[29 empty] | 2020 | April | 6 | 18 | 4 | 28500 | 0.01404%
[29 empty] | 2020 | April | 6 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 6 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 6 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 6 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 6 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 7 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 7 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 7 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 7 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 7 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 7 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 7 | 6 | 1192.5 | 28500 | 4.184%
[29 empty] | 2020 | April | 7 | 7 | 10502.5 | 28500 | 36.85%
[29 empty] | 2020 | April | 7 | 8 | 21303 | 28500 | 74.75%
[29 empty] | 2020 | April | 7 | 9 | 29695 | 28500 | 104.2%
[29 empty] | 2020 | April | 7 | 10 | 36247 | 28500 | 127.2%
[29 empty] | 2020 | April | 7 | 11 | 32726.5 | 28500 | 114.8%
[29 empty] | 2020 | April | 7 | 12 | 35752 | 28500 | 125.4%
[29 empty] | 2020 | April | 7 | 13 | 37896 | 28500 | 133%
[29 empty] | 2020 | April | 7 | 14 | 31336.5 | 28500 | 110%
[29 empty] | 2020 | April | 7 | 15 | 27730.5 | 28500 | 97.3%
[29 empty] | 2020 | April | 7 | 16 | 16045 | 28500 | 56.3%
[29 empty] | 2020 | April | 7 | 17 | 6776.5 | 28500 | 23.78%
[29 empty] | 2020 | April | 7 | 18 | 282 | 28500 | 0.9895%
[29 empty] | 2020 | April | 7 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 7 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 7 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 7 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 7 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 8 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 8 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 8 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 8 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 8 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 8 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 8 | 6 | 1355.5 | 28500 | 4.756%
[29 empty] | 2020 | April | 8 | 7 | 9821 | 28500 | 34.46%
[29 empty] | 2020 | April | 8 | 8 | 20316.5 | 28500 | 71.29%
[29 empty] | 2020 | April | 8 | 9 | 28985 | 28500 | 101.7%
[29 empty] | 2020 | April | 8 | 10 | 30943 | 28500 | 108.6%
[29 empty] | 2020 | April | 8 | 11 | 38562.5 | 28500 | 135.3%
[29 empty] | 2020 | April | 8 | 12 | 27829 | 28500 | 97.65%
[29 empty] | 2020 | April | 8 | 13 | 28644.5 | 28500 | 100.5%
[29 empty] | 2020 | April | 8 | 14 | 17780.5 | 28500 | 62.39%
[29 empty] | 2020 | April | 8 | 15 | 16944.5 | 28500 | 59.45%
[29 empty] | 2020 | April | 8 | 16 | 9231.5 | 28500 | 32.39%
[29 empty] | 2020 | April | 8 | 17 | 3946.5 | 28500 | 13.85%
[29 empty] | 2020 | April | 8 | 18 | 73.5 | 28500 | 0.2579%
[29 empty] | 2020 | April | 8 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 8 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 8 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 8 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 8 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 9 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 9 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 9 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 9 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 9 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 9 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 9 | 6 | 1397.5 | 28500 | 4.904%
[29 empty] | 2020 | April | 9 | 7 | 9929 | 28500 | 34.84%
[29 empty] | 2020 | April | 9 | 8 | 20621.5 | 28500 | 72.36%
[29 empty] | 2020 | April | 9 | 9 | 29304.5 | 28500 | 102.8%
[29 empty] | 2020 | April | 9 | 10 | 36257 | 28500 | 127.2%
[29 empty] | 2020 | April | 9 | 11 | 39871.5 | 28500 | 139.9%
[29 empty] | 2020 | April | 9 | 12 | 41522 | 28500 | 145.7%
[29 empty] | 2020 | April | 9 | 13 | 38880 | 28500 | 136.4%
[29 empty] | 2020 | April | 9 | 14 | 33663.5 | 28500 | 118.1%
[29 empty] | 2020 | April | 9 | 15 | 25805.5 | 28500 | 90.55%
[29 empty] | 2020 | April | 9 | 16 | 16892.5 | 28500 | 59.27%
[29 empty] | 2020 | April | 9 | 17 | 6421.5 | 28500 | 22.53%
[29 empty] | 2020 | April | 9 | 18 | 469.5 | 28500 | 1.647%
[29 empty] | 2020 | April | 9 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 9 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 9 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 9 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 9 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 10 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 10 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 10 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 10 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 10 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 10 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 10 | 6 | 1466.5 | 28500 | 5.146%
[29 empty] | 2020 | April | 10 | 7 | 10275 | 28500 | 36.05%
[29 empty] | 2020 | April | 10 | 8 | 21681 | 28500 | 76.07%
[29 empty] | 2020 | April | 10 | 9 | 30585 | 28500 | 107.3%
[29 empty] | 2020 | April | 10 | 10 | 36665.5 | 28500 | 128.7%
[29 empty] | 2020 | April | 10 | 11 | 40021 | 28500 | 140.4%
[29 empty] | 2020 | April | 10 | 12 | 41088.5 | 28500 | 144.2%
[29 empty] | 2020 | April | 10 | 13 | 39149.5 | 28500 | 137.4%
[29 empty] | 2020 | April | 10 | 14 | 34282 | 28500 | 120.3%
[29 empty] | 2020 | April | 10 | 15 | 27036.5 | 28500 | 94.86%
[29 empty] | 2020 | April | 10 | 16 | 17584 | 28500 | 61.7%
[29 empty] | 2020 | April | 10 | 17 | 6599.5 | 28500 | 23.16%
[29 empty] | 2020 | April | 10 | 18 | 495 | 28500 | 1.737%
[29 empty] | 2020 | April | 10 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 10 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 10 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 10 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 10 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 11 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 11 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 11 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 11 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 11 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 11 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 11 | 6 | 1606 | 28500 | 5.635%
[29 empty] | 2020 | April | 11 | 7 | 10449.5 | 28500 | 36.66%
[29 empty] | 2020 | April | 11 | 8 | 20891.5 | 28500 | 73.3%
[29 empty] | 2020 | April | 11 | 9 | 29154.5 | 28500 | 102.3%
[29 empty] | 2020 | April | 11 | 10 | 34934.5 | 28500 | 122.6%
[29 empty] | 2020 | April | 11 | 11 | 38297 | 28500 | 134.4%
[29 empty] | 2020 | April | 11 | 12 | 39321 | 28500 | 138%
[29 empty] | 2020 | April | 11 | 13 | 36353.5 | 28500 | 127.6%
[29 empty] | 2020 | April | 11 | 14 | 9880 | 28500 | 34.67%
[29 empty] | 2020 | April | 11 | 15 | 12157 | 28500 | 42.66%
[29 empty] | 2020 | April | 11 | 16 | 12531 | 28500 | 43.97%
[29 empty] | 2020 | April | 11 | 17 | 6430.5 | 28500 | 22.56%
[29 empty] | 2020 | April | 11 | 18 | 541 | 28500 | 1.898%
[29 empty] | 2020 | April | 11 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 11 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 11 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 11 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 11 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 12 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 12 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 12 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 12 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 12 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 12 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 12 | 6 | 1594 | 28500 | 5.593%
[29 empty] | 2020 | April | 12 | 7 | 8707.5 | 28500 | 30.55%
[29 empty] | 2020 | April | 12 | 8 | 20683 | 28500 | 72.57%
[29 empty] | 2020 | April | 12 | 9 | 26931 | 28500 | 94.49%
[29 empty] | 2020 | April | 12 | 10 | 32467.5 | 28500 | 113.9%
[29 empty] | 2020 | April | 12 | 11 | 32082.5 | 28500 | 112.6%
[29 empty] | 2020 | April | 12 | 12 | 33671 | 28500 | 118.1%
[29 empty] | 2020 | April | 12 | 13 | 33666.5 | 28500 | 118.1%
[29 empty] | 2020 | April | 12 | 14 | 27144 | 28500 | 95.24%
[29 empty] | 2020 | April | 12 | 15 | 26349 | 28500 | 92.45%
[29 empty] | 2020 | April | 12 | 16 | 15928.5 | 28500 | 55.89%
[29 empty] | 2020 | April | 12 | 17 | 6813.5 | 28500 | 23.91%
[29 empty] | 2020 | April | 12 | 18 | 485 | 28500 | 1.702%
[29 empty] | 2020 | April | 12 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 12 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 12 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 12 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 12 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 13 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 13 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 13 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 13 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 13 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 13 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 13 | 6 | 396.5 | 28500 | 1.391%
[29 empty] | 2020 | April | 13 | 7 | 2847 | 28500 | 9.989%
[29 empty] | 2020 | April | 13 | 8 | 6775 | 28500 | 23.77%
[29 empty] | 2020 | April | 13 | 9 | 10234 | 28500 | 35.91%
[29 empty] | 2020 | April | 13 | 10 | 23362 | 28500 | 81.97%
[29 empty] | 2020 | April | 13 | 11 | 21381.5 | 28500 | 75.02%
[29 empty] | 2020 | April | 13 | 12 | 34941.5 | 28500 | 122.6%
[29 empty] | 2020 | April | 13 | 13 | 40358 | 28500 | 141.6%
[29 empty] | 2020 | April | 13 | 14 | 27947.5 | 28500 | 98.06%
[29 empty] | 2020 | April | 13 | 15 | 30361 | 28500 | 106.5%
[29 empty] | 2020 | April | 13 | 16 | 18497.5 | 28500 | 64.9%
[29 empty] | 2020 | April | 13 | 17 | 7804 | 28500 | 27.38%
[29 empty] | 2020 | April | 13 | 18 | 667.5 | 28500 | 2.342%
[29 empty] | 2020 | April | 13 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 13 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 13 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 13 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 13 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 14 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 14 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 14 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 14 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 14 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 14 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 14 | 6 | 1945 | 28500 | 6.825%
[29 empty] | 2020 | April | 14 | 7 | 10803.5 | 28500 | 37.91%
[29 empty] | 2020 | April | 14 | 8 | 14397 | 28500 | 50.52%
[29 empty] | 2020 | April | 14 | 9 | 22493.5 | 28500 | 78.92%
[29 empty] | 2020 | April | 14 | 10 | 29954.5 | 28500 | 105.1%
[29 empty] | 2020 | April | 14 | 11 | 42068.5 | 28500 | 147.6%
[29 empty] | 2020 | April | 14 | 12 | 43459.5 | 28500 | 152.5%
[29 empty] | 2020 | April | 14 | 13 | 41393 | 28500 | 145.2%
[29 empty] | 2020 | April | 14 | 14 | 36547 | 28500 | 128.2%
[29 empty] | 2020 | April | 14 | 15 | 29198 | 28500 | 102.4%
[29 empty] | 2020 | April | 14 | 16 | 19222 | 28500 | 67.45%
[29 empty] | 2020 | April | 14 | 17 | 7630.5 | 28500 | 26.77%
[29 empty] | 2020 | April | 14 | 18 | 662 | 28500 | 2.323%
[29 empty] | 2020 | April | 14 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 14 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 14 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 14 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 14 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 15 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 15 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 15 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 15 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 15 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 15 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 15 | 6 | 1834 | 28500 | 6.435%
[29 empty] | 2020 | April | 15 | 7 | 11989.5 | 28500 | 42.07%
[29 empty] | 2020 | April | 15 | 8 | 23037.5 | 28500 | 80.83%
[29 empty] | 2020 | April | 15 | 9 | 31207 | 28500 | 109.5%
[29 empty] | 2020 | April | 15 | 10 | 36160 | 28500 | 126.9%
[29 empty] | 2020 | April | 15 | 11 | 38715 | 28500 | 135.8%
[29 empty] | 2020 | April | 15 | 12 | 41796.5 | 28500 | 146.7%
[29 empty] | 2020 | April | 15 | 13 | 40584 | 28500 | 142.4%
[29 empty] | 2020 | April | 15 | 14 | 35658 | 28500 | 125.1%
[29 empty] | 2020 | April | 15 | 15 | 28196.5 | 28500 | 98.94%
[29 empty] | 2020 | April | 15 | 16 | 18631 | 28500 | 65.37%
[29 empty] | 2020 | April | 15 | 17 | 7407.5 | 28500 | 25.99%
[29 empty] | 2020 | April | 15 | 18 | 680 | 28500 | 2.386%
[29 empty] | 2020 | April | 15 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 15 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 15 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 15 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 15 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 16 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 16 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 16 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 16 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 16 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 16 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 16 | 6 | 2231.5 | 28500 | 7.83%
[29 empty] | 2020 | April | 16 | 7 | 8523.5 | 28500 | 29.91%
[29 empty] | 2020 | April | 16 | 8 | 17069 | 28500 | 59.89%
[29 empty] | 2020 | April | 16 | 9 | 28873 | 28500 | 101.3%
[29 empty] | 2020 | April | 16 | 10 | 35061 | 28500 | 123%
[29 empty] | 2020 | April | 16 | 11 | 35425 | 28500 | 124.3%
[29 empty] | 2020 | April | 16 | 12 | 23085 | 28500 | 81%
[29 empty] | 2020 | April | 16 | 13 | 9783 | 28500 | 34.33%
[29 empty] | 2020 | April | 16 | 14 | 8619.5 | 28500 | 30.24%
[29 empty] | 2020 | April | 16 | 15 | 8368.5 | 28500 | 29.36%
[29 empty] | 2020 | April | 16 | 16 | 9988.5 | 28500 | 35.05%
[29 empty] | 2020 | April | 16 | 17 | 3414.5 | 28500 | 11.98%
[29 empty] | 2020 | April | 16 | 18 | 754.5 | 28500 | 2.647%
[29 empty] | 2020 | April | 16 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 16 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 16 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 16 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 16 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 17 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 17 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 17 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 17 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 17 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 17 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 17 | 6 | 2280 | 28500 | 8%
[29 empty] | 2020 | April | 17 | 7 | 10884 | 28500 | 38.19%
[29 empty] | 2020 | April | 17 | 8 | 13649 | 28500 | 47.89%
[29 empty] | 2020 | April | 17 | 9 | 24686.5 | 28500 | 86.62%
[29 empty] | 2020 | April | 17 | 10 | 17733 | 28500 | 62.22%
[29 empty] | 2020 | April | 17 | 11 | 9552.5 | 28500 | 33.52%
[29 empty] | 2020 | April | 17 | 12 | 19651 | 28500 | 68.95%
[29 empty] | 2020 | April | 17 | 13 | 12550.5 | 28500 | 44.04%
[29 empty] | 2020 | April | 17 | 14 | 4208.5 | 28500 | 14.77%
[29 empty] | 2020 | April | 17 | 15 | 5316 | 28500 | 18.65%
[29 empty] | 2020 | April | 17 | 16 | 3722.5 | 28500 | 13.06%
[29 empty] | 2020 | April | 17 | 17 | 5569 | 28500 | 19.54%
[29 empty] | 2020 | April | 17 | 18 | 571 | 28500 | 2.004%
[29 empty] | 2020 | April | 17 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 17 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 17 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 17 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 17 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 18 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 18 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 18 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 18 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 18 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 18 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 18 | 6 | 2102 | 28500 | 7.375%
[29 empty] | 2020 | April | 18 | 7 | 9304.5 | 28500 | 32.65%
[29 empty] | 2020 | April | 18 | 8 | 7355.5 | 28500 | 25.81%
[29 empty] | 2020 | April | 18 | 9 | 6145.5 | 28500 | 21.56%
[29 empty] | 2020 | April | 18 | 10 | 4737.5 | 28500 | 16.62%
[29 empty] | 2020 | April | 18 | 11 | 6445.5 | 28500 | 22.62%
[29 empty] | 2020 | April | 18 | 12 | 14840.5 | 28500 | 52.07%
[29 empty] | 2020 | April | 18 | 13 | 11939.5 | 28500 | 41.89%
[29 empty] | 2020 | April | 18 | 14 | 7955.5 | 28500 | 27.91%
[29 empty] | 2020 | April | 18 | 15 | 6605 | 28500 | 23.18%
[29 empty] | 2020 | April | 18 | 16 | 7142.5 | 28500 | 25.06%
[29 empty] | 2020 | April | 18 | 17 | 4024.5 | 28500 | 14.12%
[29 empty] | 2020 | April | 18 | 18 | 828.5 | 28500 | 2.907%
[29 empty] | 2020 | April | 18 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 18 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 18 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 18 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 18 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 19 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 19 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 19 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 19 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 19 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 19 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 19 | 6 | 2462 | 28500 | 8.639%
[29 empty] | 2020 | April | 19 | 7 | 12457.5 | 28500 | 43.71%
[29 empty] | 2020 | April | 19 | 8 | 24034.5 | 28500 | 84.33%
[29 empty] | 2020 | April | 19 | 9 | 32998.5 | 28500 | 115.8%
[29 empty] | 2020 | April | 19 | 10 | 39324.5 | 28500 | 138%
[29 empty] | 2020 | April | 19 | 11 | 43581 | 28500 | 152.9%
[29 empty] | 2020 | April | 19 | 12 | 44102.5 | 28500 | 154.7%
[29 empty] | 2020 | April | 19 | 13 | 41770.5 | 28500 | 146.6%
[29 empty] | 2020 | April | 19 | 14 | 36658.5 | 28500 | 128.6%
[29 empty] | 2020 | April | 19 | 15 | 29069.5 | 28500 | 102%
[29 empty] | 2020 | April | 19 | 16 | 19129.5 | 28500 | 67.12%
[29 empty] | 2020 | April | 19 | 17 | 7669 | 28500 | 26.91%
[29 empty] | 2020 | April | 19 | 18 | 802.5 | 28500 | 2.816%
[29 empty] | 2020 | April | 19 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 19 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 19 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 19 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 19 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 20 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 20 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 20 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 20 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 20 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 20 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 20 | 6 | 2319.5 | 28500 | 8.139%
[29 empty] | 2020 | April | 20 | 7 | 13001.5 | 28500 | 45.62%
[29 empty] | 2020 | April | 20 | 8 | 24390.5 | 28500 | 85.58%
[29 empty] | 2020 | April | 20 | 9 | 34155 | 28500 | 119.8%
[29 empty] | 2020 | April | 20 | 10 | 40738 | 28500 | 142.9%
[29 empty] | 2020 | April | 20 | 11 | 44435 | 28500 | 155.9%
[29 empty] | 2020 | April | 20 | 12 | 45451.5 | 28500 | 159.5%
[29 empty] | 2020 | April | 20 | 13 | 43060.5 | 28500 | 151.1%
[29 empty] | 2020 | April | 20 | 14 | 37531 | 28500 | 131.7%
[29 empty] | 2020 | April | 20 | 15 | 29678.5 | 28500 | 104.1%
[29 empty] | 2020 | April | 20 | 16 | 19468 | 28500 | 68.31%
[29 empty] | 2020 | April | 20 | 17 | 7803.5 | 28500 | 27.38%
[29 empty] | 2020 | April | 20 | 18 | 862 | 28500 | 3.025%
[29 empty] | 2020 | April | 20 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 20 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 20 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 20 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 20 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 21 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 21 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 21 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 21 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 21 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 21 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 21 | 6 | 2393 | 28500 | 8.396%
[29 empty] | 2020 | April | 21 | 7 | 12850.5 | 28500 | 45.09%
[29 empty] | 2020 | April | 21 | 8 | 24340 | 28500 | 85.4%
[29 empty] | 2020 | April | 21 | 9 | 33815.5 | 28500 | 118.7%
[29 empty] | 2020 | April | 21 | 10 | 40351 | 28500 | 141.6%
[29 empty] | 2020 | April | 21 | 11 | 44159 | 28500 | 154.9%
[29 empty] | 2020 | April | 21 | 12 | 45243.5 | 28500 | 158.7%
[29 empty] | 2020 | April | 21 | 13 | 42475.5 | 28500 | 149%
[29 empty] | 2020 | April | 21 | 14 | 37117.5 | 28500 | 130.2%
[29 empty] | 2020 | April | 21 | 15 | 29098 | 28500 | 102.1%
[29 empty] | 2020 | April | 21 | 16 | 18727 | 28500 | 65.71%
[29 empty] | 2020 | April | 21 | 17 | 7544 | 28500 | 26.47%
[29 empty] | 2020 | April | 21 | 18 | 1043.5 | 28500 | 3.661%
[29 empty] | 2020 | April | 21 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 21 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 21 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 21 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 21 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 22 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 22 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 22 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 22 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 22 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 22 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 22 | 6 | 2553.5 | 28500 | 8.96%
[29 empty] | 2020 | April | 22 | 7 | 13025.5 | 28500 | 45.7%
[29 empty] | 2020 | April | 22 | 8 | 24118 | 28500 | 84.62%
[29 empty] | 2020 | April | 22 | 9 | 33042.5 | 28500 | 115.9%
[29 empty] | 2020 | April | 22 | 10 | 39668 | 28500 | 139.2%
[29 empty] | 2020 | April | 22 | 11 | 43512 | 28500 | 152.7%
[29 empty] | 2020 | April | 22 | 12 | 44342.5 | 28500 | 155.6%
[29 empty] | 2020 | April | 22 | 13 | 41795 | 28500 | 146.6%
[29 empty] | 2020 | April | 22 | 14 | 36891.5 | 28500 | 129.4%
[29 empty] | 2020 | April | 22 | 15 | 29227 | 28500 | 102.6%
[29 empty] | 2020 | April | 22 | 16 | 19064.5 | 28500 | 66.89%
[29 empty] | 2020 | April | 22 | 17 | 7736.5 | 28500 | 27.15%
[29 empty] | 2020 | April | 22 | 18 | 976 | 28500 | 3.425%
[29 empty] | 2020 | April | 22 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 22 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 22 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 22 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 22 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 23 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 23 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 23 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 23 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 23 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 23 | 5 | 5.5 | 28500 | 0.0193%
[29 empty] | 2020 | April | 23 | 6 | 2713.5 | 28500 | 9.521%
[29 empty] | 2020 | April | 23 | 7 | 12959 | 28500 | 45.47%
[29 empty] | 2020 | April | 23 | 8 | 23674 | 28500 | 83.07%
[29 empty] | 2020 | April | 23 | 9 | 32438.5 | 28500 | 113.8%
[29 empty] | 2020 | April | 23 | 10 | 38360 | 28500 | 134.6%
[29 empty] | 2020 | April | 23 | 11 | 41887 | 28500 | 147%
[29 empty] | 2020 | April | 23 | 12 | 42405 | 28500 | 148.8%
[29 empty] | 2020 | April | 23 | 13 | 39764 | 28500 | 139.5%
[29 empty] | 2020 | April | 23 | 14 | 34990.5 | 28500 | 122.8%
[29 empty] | 2020 | April | 23 | 15 | 27612.5 | 28500 | 96.89%
[29 empty] | 2020 | April | 23 | 16 | 18182.5 | 28500 | 63.8%
[29 empty] | 2020 | April | 23 | 17 | 7581 | 28500 | 26.6%
[29 empty] | 2020 | April | 23 | 18 | 839 | 28500 | 2.944%
[29 empty] | 2020 | April | 23 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 23 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 23 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 23 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 23 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 24 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 24 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 24 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 24 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 24 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 24 | 5 | 40.5 | 28500 | 0.1421%
[29 empty] | 2020 | April | 24 | 6 | 2848 | 28500 | 9.993%
[29 empty] | 2020 | April | 24 | 7 | 12311.5 | 28500 | 43.2%
[29 empty] | 2020 | April | 24 | 8 | 23027.5 | 28500 | 80.8%
[29 empty] | 2020 | April | 24 | 9 | 31437.5 | 28500 | 110.3%
[29 empty] | 2020 | April | 24 | 10 | 37550.5 | 28500 | 131.8%
[29 empty] | 2020 | April | 24 | 11 | 40742 | 28500 | 143%
[29 empty] | 2020 | April | 24 | 12 | 40959 | 28500 | 143.7%
[29 empty] | 2020 | April | 24 | 13 | 38836 | 28500 | 136.3%
[29 empty] | 2020 | April | 24 | 14 | 34241 | 28500 | 120.1%
[29 empty] | 2020 | April | 24 | 15 | 26806 | 28500 | 94.06%
[29 empty] | 2020 | April | 24 | 16 | 15575.5 | 28500 | 54.65%
[29 empty] | 2020 | April | 24 | 17 | 7188 | 28500 | 25.22%
[29 empty] | 2020 | April | 24 | 18 | 1312.5 | 28500 | 4.605%
[29 empty] | 2020 | April | 24 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 24 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 24 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 24 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 24 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 25 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 25 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 25 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 25 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 25 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 25 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 25 | 6 | 2292.5 | 28500 | 8.044%
[29 empty] | 2020 | April | 25 | 7 | 5473 | 28500 | 19.2%
[29 empty] | 2020 | April | 25 | 8 | 6748.5 | 28500 | 23.68%
[29 empty] | 2020 | April | 25 | 9 | 11757 | 28500 | 41.25%
[29 empty] | 2020 | April | 25 | 10 | 12526.5 | 28500 | 43.95%
[29 empty] | 2020 | April | 25 | 11 | 39678 | 28500 | 139.2%
[29 empty] | 2020 | April | 25 | 12 | 42694 | 28500 | 149.8%
[29 empty] | 2020 | April | 25 | 13 | 40485 | 28500 | 142.1%
[29 empty] | 2020 | April | 25 | 14 | 35903.5 | 28500 | 126%
[29 empty] | 2020 | April | 25 | 15 | 28550 | 28500 | 100.2%
[29 empty] | 2020 | April | 25 | 16 | 18881.5 | 28500 | 66.25%
[29 empty] | 2020 | April | 25 | 17 | 7878 | 28500 | 27.64%
[29 empty] | 2020 | April | 25 | 18 | 923 | 28500 | 3.239%
[29 empty] | 2020 | April | 25 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 25 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 25 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 25 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 25 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 26 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 26 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 26 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 26 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 26 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 26 | 5 | 196 | 28500 | 0.6877%
[29 empty] | 2020 | April | 26 | 6 | 2766 | 28500 | 9.705%
[29 empty] | 2020 | April | 26 | 7 | 13348.5 | 28500 | 46.84%
[29 empty] | 2020 | April | 26 | 8 | 23938.5 | 28500 | 83.99%
[29 empty] | 2020 | April | 26 | 9 | 32070.5 | 28500 | 112.5%
[29 empty] | 2020 | April | 26 | 10 | 37833.5 | 28500 | 132.7%
[29 empty] | 2020 | April | 26 | 11 | 40680.5 | 28500 | 142.7%
[29 empty] | 2020 | April | 26 | 12 | 41005.5 | 28500 | 143.9%
[29 empty] | 2020 | April | 26 | 13 | 38980 | 28500 | 136.8%
[29 empty] | 2020 | April | 26 | 14 | 33376 | 28500 | 117.1%
[29 empty] | 2020 | April | 26 | 15 | 27558 | 28500 | 96.69%
[29 empty] | 2020 | April | 26 | 16 | 18248.5 | 28500 | 64.03%
[29 empty] | 2020 | April | 26 | 17 | 7659.5 | 28500 | 26.88%
[29 empty] | 2020 | April | 26 | 18 | 1028.5 | 28500 | 3.609%
[29 empty] | 2020 | April | 26 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 26 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 26 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 26 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 26 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 27 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 27 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 27 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 27 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 27 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 27 | 5 | 191.5 | 28500 | 0.6719%
[29 empty] | 2020 | April | 27 | 6 | 3136 | 28500 | 11%
[29 empty] | 2020 | April | 27 | 7 | 7846 | 28500 | 27.53%
[29 empty] | 2020 | April | 27 | 8 | 8270 | 28500 | 29.02%
[29 empty] | 2020 | April | 27 | 9 | 20007.5 | 28500 | 70.2%
[29 empty] | 2020 | April | 27 | 10 | 9174 | 28500 | 32.19%
[29 empty] | 2020 | April | 27 | 11 | 26211 | 28500 | 91.97%
[29 empty] | 2020 | April | 27 | 12 | 15503 | 28500 | 54.4%
[29 empty] | 2020 | April | 27 | 13 | 20601.5 | 28500 | 72.29%
[29 empty] | 2020 | April | 27 | 14 | 26601.5 | 28500 | 93.34%
[29 empty] | 2020 | April | 27 | 15 | 21497.5 | 28500 | 75.43%
[29 empty] | 2020 | April | 27 | 16 | 14762 | 28500 | 51.8%
[29 empty] | 2020 | April | 27 | 17 | 5307.5 | 28500 | 18.62%
[29 empty] | 2020 | April | 27 | 18 | 577.5 | 28500 | 2.026%
[29 empty] | 2020 | April | 27 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 27 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 27 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 27 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 27 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 28 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 28 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 28 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 28 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 28 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 28 | 5 | 121 | 28500 | 0.4246%
[29 empty] | 2020 | April | 28 | 6 | 2686 | 28500 | 9.425%
[29 empty] | 2020 | April | 28 | 7 | 707 | 28500 | 2.481%
[29 empty] | 2020 | April | 28 | 8 | 1725.5 | 28500 | 6.054%
[29 empty] | 2020 | April | 28 | 9 | 3165.5 | 28500 | 11.11%
[29 empty] | 2020 | April | 28 | 10 | 3869 | 28500 | 13.58%
[29 empty] | 2020 | April | 28 | 11 | 4694.5 | 28500 | 16.47%
[29 empty] | 2020 | April | 28 | 12 | 4058 | 28500 | 14.24%
[29 empty] | 2020 | April | 28 | 13 | 3624 | 28500 | 12.72%
[29 empty] | 2020 | April | 28 | 14 | 1755 | 28500 | 6.158%
[29 empty] | 2020 | April | 28 | 15 | 4138 | 28500 | 14.52%
[29 empty] | 2020 | April | 28 | 16 | 9314.5 | 28500 | 32.68%
[29 empty] | 2020 | April | 28 | 17 | 1397 | 28500 | 4.902%
[29 empty] | 2020 | April | 28 | 18 | 753 | 28500 | 2.642%
[29 empty] | 2020 | April | 28 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 28 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 28 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 28 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 28 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 29 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 29 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 29 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 29 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 29 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 29 | 5 | 39.5 | 28500 | 0.1386%
[29 empty] | 2020 | April | 29 | 6 | 1220.5 | 28500 | 4.282%
[29 empty] | 2020 | April | 29 | 7 | 13006.5 | 28500 | 45.64%
[29 empty] | 2020 | April | 29 | 8 | 13746.5 | 28500 | 48.23%
[29 empty] | 2020 | April | 29 | 9 | 23619 | 28500 | 82.87%
[29 empty] | 2020 | April | 29 | 10 | 10227.5 | 28500 | 35.89%
[29 empty] | 2020 | April | 29 | 11 | 13277 | 28500 | 46.59%
[29 empty] | 2020 | April | 29 | 12 | 12783.5 | 28500 | 44.85%
[29 empty] | 2020 | April | 29 | 13 | 6867 | 28500 | 24.09%
[29 empty] | 2020 | April | 29 | 14 | 5614 | 28500 | 19.7%
[29 empty] | 2020 | April | 29 | 15 | 8924 | 28500 | 31.31%
[29 empty] | 2020 | April | 29 | 16 | 7068 | 28500 | 24.8%
[29 empty] | 2020 | April | 29 | 17 | 4339.5 | 28500 | 15.23%
[29 empty] | 2020 | April | 29 | 18 | 1409.5 | 28500 | 4.946%
[29 empty] | 2020 | April | 29 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 29 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 29 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 29 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 29 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 30 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 30 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 30 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 30 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 30 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 30 | 5 | 405.5 | 28500 | 1.423%
[29 empty] | 2020 | April | 30 | 6 | 3267 | 28500 | 11.46%
[29 empty] | 2020 | April | 30 | 7 | 3253.5 | 28500 | 11.42%
[29 empty] | 2020 | April | 30 | 8 | 8321.5 | 28500 | 29.2%
[29 empty] | 2020 | April | 30 | 9 | 21296.5 | 28500 | 74.72%
[29 empty] | 2020 | April | 30 | 10 | 20387 | 28500 | 71.53%
[29 empty] | 2020 | April | 30 | 11 | 26333.5 | 28500 | 92.4%
[29 empty] | 2020 | April | 30 | 12 | 13087.5 | 28500 | 45.92%
[29 empty] | 2020 | April | 30 | 13 | 5944 | 28500 | 20.86%
[29 empty] | 2020 | April | 30 | 14 | 2679 | 28500 | 9.4%
[29 empty] | 2020 | April | 30 | 15 | 15699.5 | 28500 | 55.09%
[29 empty] | 2020 | April | 30 | 16 | 8334 | 28500 | 29.24%
[29 empty] | 2020 | April | 30 | 17 | 7763 | 28500 | 27.24%
[29 empty] | 2020 | April | 30 | 18 | 1094.5 | 28500 | 3.84%
[29 empty] | 2020 | April | 30 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 30 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 30 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 30 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | April | 30 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 1 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 1 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 1 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 1 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 1 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 1 | 5 | 295 | 28500 | 1.035%
[29 empty] | 2020 | May | 1 | 6 | 1658 | 28500 | 5.818%
[29 empty] | 2020 | May | 1 | 7 | 7305.5 | 28500 | 25.63%
[29 empty] | 2020 | May | 1 | 8 | 18906 | 28500 | 66.34%
[29 empty] | 2020 | May | 1 | 9 | 22073 | 28500 | 77.45%
[29 empty] | 2020 | May | 1 | 10 | 21966 | 28500 | 77.07%
[29 empty] | 2020 | May | 1 | 11 | 39035 | 28500 | 137%
[29 empty] | 2020 | May | 1 | 12 | 3392 | 28500 | 11.9%
[29 empty] | 2020 | May | 1 | 13 | 40302 | 28500 | 141.4%
[29 empty] | 2020 | May | 1 | 14 | 7887.5 | 28500 | 27.68%
[29 empty] | 2020 | May | 1 | 15 | 16808 | 28500 | 58.98%
[29 empty] | 2020 | May | 1 | 16 | 16957 | 28500 | 59.5%
[29 empty] | 2020 | May | 1 | 17 | 3981 | 28500 | 13.97%
[29 empty] | 2020 | May | 1 | 18 | 1082.5 | 28500 | 3.798%
[29 empty] | 2020 | May | 1 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 1 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 1 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 1 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 1 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 2 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 2 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 2 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 2 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 2 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 2 | 5 | 551 | 28500 | 1.933%
[29 empty] | 2020 | May | 2 | 6 | 3067.5 | 28500 | 10.76%
[29 empty] | 2020 | May | 2 | 7 | 14046.5 | 28500 | 49.29%
[29 empty] | 2020 | May | 2 | 8 | 23200.5 | 28500 | 81.41%
[29 empty] | 2020 | May | 2 | 9 | 30028 | 28500 | 105.4%
[29 empty] | 2020 | May | 2 | 10 | 34441 | 28500 | 120.8%
[29 empty] | 2020 | May | 2 | 11 | 36464.5 | 28500 | 127.9%
[29 empty] | 2020 | May | 2 | 12 | 34305.5 | 28500 | 120.4%
[29 empty] | 2020 | May | 2 | 13 | 24806 | 28500 | 87.04%
[29 empty] | 2020 | May | 2 | 14 | 22614 | 28500 | 79.35%
[29 empty] | 2020 | May | 2 | 15 | 19818.5 | 28500 | 69.54%
[29 empty] | 2020 | May | 2 | 16 | 11668 | 28500 | 40.94%
[29 empty] | 2020 | May | 2 | 17 | 5827.5 | 28500 | 20.45%
[29 empty] | 2020 | May | 2 | 18 | 1793.5 | 28500 | 6.293%
[29 empty] | 2020 | May | 2 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 2 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 2 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 2 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 2 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 3 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 3 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 3 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 3 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 3 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 3 | 5 | 579 | 28500 | 2.032%
[29 empty] | 2020 | May | 3 | 6 | 2537 | 28500 | 8.902%
[29 empty] | 2020 | May | 3 | 7 | 8577.5 | 28500 | 30.1%
[29 empty] | 2020 | May | 3 | 8 | 12755.5 | 28500 | 44.76%
[29 empty] | 2020 | May | 3 | 9 | 13813.5 | 28500 | 48.47%
[29 empty] | 2020 | May | 3 | 10 | 9688.5 | 28500 | 33.99%
[29 empty] | 2020 | May | 3 | 11 | 9953 | 28500 | 34.92%
[29 empty] | 2020 | May | 3 | 12 | 9187 | 28500 | 32.24%
[29 empty] | 2020 | May | 3 | 13 | 5226.5 | 28500 | 18.34%
[29 empty] | 2020 | May | 3 | 14 | 4797 | 28500 | 16.83%
[29 empty] | 2020 | May | 3 | 15 | 4679.5 | 28500 | 16.42%
[29 empty] | 2020 | May | 3 | 16 | 5116.5 | 28500 | 17.95%
[29 empty] | 2020 | May | 3 | 17 | 3148.5 | 28500 | 11.05%
[29 empty] | 2020 | May | 3 | 18 | 1010.5 | 28500 | 3.546%
[29 empty] | 2020 | May | 3 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 3 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 3 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 3 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 3 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 4 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 4 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 4 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 4 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 4 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 4 | 5 | 58 | 28500 | 0.2035%
[29 empty] | 2020 | May | 4 | 6 | 3683.5 | 28500 | 12.92%
[29 empty] | 2020 | May | 4 | 7 | 10358 | 28500 | 36.34%
[29 empty] | 2020 | May | 4 | 8 | 21131 | 28500 | 74.14%
[29 empty] | 2020 | May | 4 | 9 | 28630 | 28500 | 100.5%
[29 empty] | 2020 | May | 4 | 10 | 24173.5 | 28500 | 84.82%
[29 empty] | 2020 | May | 4 | 11 | 37493.5 | 28500 | 131.6%
[29 empty] | 2020 | May | 4 | 12 | 38066.5 | 28500 | 133.6%
[29 empty] | 2020 | May | 4 | 13 | 39818 | 28500 | 139.7%
[29 empty] | 2020 | May | 4 | 14 | 35865.5 | 28500 | 125.8%
[29 empty] | 2020 | May | 4 | 15 | 28419 | 28500 | 99.72%
[29 empty] | 2020 | May | 4 | 16 | 18622.5 | 28500 | 65.34%
[29 empty] | 2020 | May | 4 | 17 | 7959.5 | 28500 | 27.93%
[29 empty] | 2020 | May | 4 | 18 | 1911.5 | 28500 | 6.707%
[29 empty] | 2020 | May | 4 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 4 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 4 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 4 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 4 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 5 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 5 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 5 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 5 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 5 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 5 | 5 | 517 | 28500 | 1.814%
[29 empty] | 2020 | May | 5 | 6 | 3600.5 | 28500 | 12.63%
[29 empty] | 2020 | May | 5 | 7 | 6863.5 | 28500 | 24.08%
[29 empty] | 2020 | May | 5 | 8 | 17385.5 | 28500 | 61%
[29 empty] | 2020 | May | 5 | 9 | 22389.5 | 28500 | 78.56%
[29 empty] | 2020 | May | 5 | 10 | 35580 | 28500 | 124.8%
[29 empty] | 2020 | May | 5 | 11 | 42204.5 | 28500 | 148.1%
[29 empty] | 2020 | May | 5 | 12 | 44384.5 | 28500 | 155.7%
[29 empty] | 2020 | May | 5 | 13 | 42583 | 28500 | 149.4%
[29 empty] | 2020 | May | 5 | 14 | 37126.5 | 28500 | 130.3%
[29 empty] | 2020 | May | 5 | 15 | 29753.5 | 28500 | 104.4%
[29 empty] | 2020 | May | 5 | 16 | 19792.5 | 28500 | 69.45%
[29 empty] | 2020 | May | 5 | 17 | 8434 | 28500 | 29.59%
[29 empty] | 2020 | May | 5 | 18 | 1587.5 | 28500 | 5.57%
[29 empty] | 2020 | May | 5 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 5 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 5 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 5 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 5 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 6 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 6 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 6 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 6 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 6 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 6 | 5 | 704 | 28500 | 2.47%
[29 empty] | 2020 | May | 6 | 6 | 3487 | 28500 | 12.24%
[29 empty] | 2020 | May | 6 | 7 | 14099.5 | 28500 | 49.47%
[29 empty] | 2020 | May | 6 | 8 | 24505 | 28500 | 85.98%
[29 empty] | 2020 | May | 6 | 9 | 32693.5 | 28500 | 114.7%
[29 empty] | 2020 | May | 6 | 10 | 38578 | 28500 | 135.4%
[29 empty] | 2020 | May | 6 | 11 | 42054.5 | 28500 | 147.6%
[29 empty] | 2020 | May | 6 | 12 | 42946 | 28500 | 150.7%
[29 empty] | 2020 | May | 6 | 13 | 40469.5 | 28500 | 142%
[29 empty] | 2020 | May | 6 | 14 | 35505.5 | 28500 | 124.6%
[29 empty] | 2020 | May | 6 | 15 | 28692 | 28500 | 100.7%
[29 empty] | 2020 | May | 6 | 16 | 19204.5 | 28500 | 67.38%
[29 empty] | 2020 | May | 6 | 17 | 8257.5 | 28500 | 28.97%
[29 empty] | 2020 | May | 6 | 18 | 1495 | 28500 | 5.246%
[29 empty] | 2020 | May | 6 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 6 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 6 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 6 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 6 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 7 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 7 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 7 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 7 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 7 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 7 | 5 | 795 | 28500 | 2.789%
[29 empty] | 2020 | May | 7 | 6 | 3849 | 28500 | 13.51%
[29 empty] | 2020 | May | 7 | 7 | 12987.5 | 28500 | 45.57%
[29 empty] | 2020 | May | 7 | 8 | 21901.5 | 28500 | 76.85%
[29 empty] | 2020 | May | 7 | 9 | 29976 | 28500 | 105.2%
[29 empty] | 2020 | May | 7 | 10 | 35344 | 28500 | 124%
[29 empty] | 2020 | May | 7 | 11 | 40468.5 | 28500 | 142%
[29 empty] | 2020 | May | 7 | 12 | 40423.5 | 28500 | 141.8%
[29 empty] | 2020 | May | 7 | 13 | 36688.5 | 28500 | 128.7%
[29 empty] | 2020 | May | 7 | 14 | 33229.5 | 28500 | 116.6%
[29 empty] | 2020 | May | 7 | 15 | 25933.5 | 28500 | 90.99%
[29 empty] | 2020 | May | 7 | 16 | 16878.5 | 28500 | 59.22%
[29 empty] | 2020 | May | 7 | 17 | 7885 | 28500 | 27.67%
[29 empty] | 2020 | May | 7 | 18 | 1886.5 | 28500 | 6.619%
[29 empty] | 2020 | May | 7 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 7 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 7 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 7 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 7 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 8 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 8 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 8 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 8 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 8 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 8 | 5 | 724.5 | 28500 | 2.542%
[29 empty] | 2020 | May | 8 | 6 | 3513.5 | 28500 | 12.33%
[29 empty] | 2020 | May | 8 | 7 | 13016 | 28500 | 45.67%
[29 empty] | 2020 | May | 8 | 8 | 19849.5 | 28500 | 69.65%
[29 empty] | 2020 | May | 8 | 9 | 24262 | 28500 | 85.13%
[29 empty] | 2020 | May | 8 | 10 | 26134 | 28500 | 91.7%
[29 empty] | 2020 | May | 8 | 11 | 22370 | 28500 | 78.49%
[29 empty] | 2020 | May | 8 | 12 | 39165 | 28500 | 137.4%
[29 empty] | 2020 | May | 8 | 13 | 37771.5 | 28500 | 132.5%
[29 empty] | 2020 | May | 8 | 14 | 33068.5 | 28500 | 116%
[29 empty] | 2020 | May | 8 | 15 | 26758 | 28500 | 93.89%
[29 empty] | 2020 | May | 8 | 16 | 18037 | 28500 | 63.29%
[29 empty] | 2020 | May | 8 | 17 | 7828.5 | 28500 | 27.47%
[29 empty] | 2020 | May | 8 | 18 | 1414.5 | 28500 | 4.963%
[29 empty] | 2020 | May | 8 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 8 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 8 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 8 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 8 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 9 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 9 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 9 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 9 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 9 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 9 | 5 | 844 | 28500 | 2.961%
[29 empty] | 2020 | May | 9 | 6 | 3636 | 28500 | 12.76%
[29 empty] | 2020 | May | 9 | 7 | 13306 | 28500 | 46.69%
[29 empty] | 2020 | May | 9 | 8 | 23334 | 28500 | 81.87%
[29 empty] | 2020 | May | 9 | 9 | 31255.5 | 28500 | 109.7%
[29 empty] | 2020 | May | 9 | 10 | 37652.5 | 28500 | 132.1%
[29 empty] | 2020 | May | 9 | 11 | 40945.5 | 28500 | 143.7%
[29 empty] | 2020 | May | 9 | 12 | 41160.5 | 28500 | 144.4%
[29 empty] | 2020 | May | 9 | 13 | 38972 | 28500 | 136.7%
[29 empty] | 2020 | May | 9 | 14 | 33875.5 | 28500 | 118.9%
[29 empty] | 2020 | May | 9 | 15 | 26915 | 28500 | 94.44%
[29 empty] | 2020 | May | 9 | 16 | 13762.5 | 28500 | 48.29%
[29 empty] | 2020 | May | 9 | 17 | 7476.5 | 28500 | 26.23%
[29 empty] | 2020 | May | 9 | 18 | 1886 | 28500 | 6.618%
[29 empty] | 2020 | May | 9 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 9 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 9 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 9 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 9 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 10 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 10 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 10 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 10 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 10 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 10 | 5 | 927.5 | 28500 | 3.254%
[29 empty] | 2020 | May | 10 | 6 | 4214 | 28500 | 14.79%
[29 empty] | 2020 | May | 10 | 7 | 10523 | 28500 | 36.92%
[29 empty] | 2020 | May | 10 | 8 | 12948.5 | 28500 | 45.43%
[29 empty] | 2020 | May | 10 | 9 | 20568 | 28500 | 72.17%
[29 empty] | 2020 | May | 10 | 10 | 27005 | 28500 | 94.75%
[29 empty] | 2020 | May | 10 | 11 | 19789 | 28500 | 69.44%
[29 empty] | 2020 | May | 10 | 12 | 9567.5 | 28500 | 33.57%
[29 empty] | 2020 | May | 10 | 13 | 5450 | 28500 | 19.12%
[29 empty] | 2020 | May | 10 | 14 | 2617 | 28500 | 9.182%
[29 empty] | 2020 | May | 10 | 15 | 2419.5 | 28500 | 8.489%
[29 empty] | 2020 | May | 10 | 16 | 2111 | 28500 | 7.407%
[29 empty] | 2020 | May | 10 | 17 | 1684.5 | 28500 | 5.911%
[29 empty] | 2020 | May | 10 | 18 | 401 | 28500 | 1.407%
[29 empty] | 2020 | May | 10 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 10 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 10 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 10 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 10 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 11 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 11 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 11 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 11 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 11 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 11 | 5 | 735 | 28500 | 2.579%
[29 empty] | 2020 | May | 11 | 6 | 3753 | 28500 | 13.17%
[29 empty] | 2020 | May | 11 | 7 | 14115.5 | 28500 | 49.53%
[29 empty] | 2020 | May | 11 | 8 | 23588.5 | 28500 | 82.77%
[29 empty] | 2020 | May | 11 | 9 | 16795 | 28500 | 58.93%
[29 empty] | 2020 | May | 11 | 10 | 16816.5 | 28500 | 59.01%
[29 empty] | 2020 | May | 11 | 11 | 20360 | 28500 | 71.44%
[29 empty] | 2020 | May | 11 | 12 | 23850.5 | 28500 | 83.69%
[29 empty] | 2020 | May | 11 | 13 | 13654.5 | 28500 | 47.91%
[29 empty] | 2020 | May | 11 | 14 | 17934 | 28500 | 62.93%
[29 empty] | 2020 | May | 11 | 15 | 17315.5 | 28500 | 60.76%
[29 empty] | 2020 | May | 11 | 16 | 16116 | 28500 | 56.55%
[29 empty] | 2020 | May | 11 | 17 | 8719 | 28500 | 30.59%
[29 empty] | 2020 | May | 11 | 18 | 2362.5 | 28500 | 8.289%
[29 empty] | 2020 | May | 11 | 19 | 21.5 | 28500 | 0.07544%
[29 empty] | 2020 | May | 11 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 11 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 11 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 11 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 12 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 12 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 12 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 12 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 12 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 12 | 5 | 903.5 | 28500 | 3.17%
[29 empty] | 2020 | May | 12 | 6 | 3653 | 28500 | 12.82%
[29 empty] | 2020 | May | 12 | 7 | 14849.5 | 28500 | 52.1%
[29 empty] | 2020 | May | 12 | 8 | 25238.5 | 28500 | 88.56%
[29 empty] | 2020 | May | 12 | 9 | 33533 | 28500 | 117.7%
[29 empty] | 2020 | May | 12 | 10 | 38274 | 28500 | 134.3%
[29 empty] | 2020 | May | 12 | 11 | 37848.5 | 28500 | 132.8%
[29 empty] | 2020 | May | 12 | 12 | 31381 | 28500 | 110.1%
[29 empty] | 2020 | May | 12 | 13 | 31021 | 28500 | 108.8%
[29 empty] | 2020 | May | 12 | 14 | 23447.5 | 28500 | 82.27%
[29 empty] | 2020 | May | 12 | 15 | 20010.5 | 28500 | 70.21%
[29 empty] | 2020 | May | 12 | 16 | 17092 | 28500 | 59.97%
[29 empty] | 2020 | May | 12 | 17 | 8353 | 28500 | 29.31%
[29 empty] | 2020 | May | 12 | 18 | 1886.5 | 28500 | 6.619%
[29 empty] | 2020 | May | 12 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 12 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 12 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 12 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 12 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 13 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 13 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 13 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 13 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 13 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 13 | 5 | 1087 | 28500 | 3.814%
[29 empty] | 2020 | May | 13 | 6 | 4620 | 28500 | 16.21%
[29 empty] | 2020 | May | 13 | 7 | 9403 | 28500 | 32.99%
[29 empty] | 2020 | May | 13 | 8 | 6933 | 28500 | 24.33%
[29 empty] | 2020 | May | 13 | 9 | 13205.5 | 28500 | 46.34%
[29 empty] | 2020 | May | 13 | 10 | 8066.5 | 28500 | 28.3%
[29 empty] | 2020 | May | 13 | 11 | 7199 | 28500 | 25.26%
[29 empty] | 2020 | May | 13 | 12 | 6140.5 | 28500 | 21.55%
[29 empty] | 2020 | May | 13 | 13 | 11583.5 | 28500 | 40.64%
[29 empty] | 2020 | May | 13 | 14 | 12568 | 28500 | 44.1%
[29 empty] | 2020 | May | 13 | 15 | 22174 | 28500 | 77.8%
[29 empty] | 2020 | May | 13 | 16 | 10522.5 | 28500 | 36.92%
[29 empty] | 2020 | May | 13 | 17 | 3118.5 | 28500 | 10.94%
[29 empty] | 2020 | May | 13 | 18 | 1043 | 28500 | 3.66%
[29 empty] | 2020 | May | 13 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 13 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 13 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 13 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 13 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 14 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 14 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 14 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 14 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 14 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 14 | 5 | 966.5 | 28500 | 3.391%
[29 empty] | 2020 | May | 14 | 6 | 3721.5 | 28500 | 13.06%
[29 empty] | 2020 | May | 14 | 7 | 13045 | 28500 | 45.77%
[29 empty] | 2020 | May | 14 | 8 | 16869.5 | 28500 | 59.19%
[29 empty] | 2020 | May | 14 | 9 | 20015 | 28500 | 70.23%
[29 empty] | 2020 | May | 14 | 10 | 14119.5 | 28500 | 49.54%
[29 empty] | 2020 | May | 14 | 11 | 6108.5 | 28500 | 21.43%
[29 empty] | 2020 | May | 14 | 12 | 15429 | 28500 | 54.14%
[29 empty] | 2020 | May | 14 | 13 | 14755.5 | 28500 | 51.77%
[29 empty] | 2020 | May | 14 | 14 | 20736.5 | 28500 | 72.76%
[29 empty] | 2020 | May | 14 | 15 | 21944.5 | 28500 | 77%
[29 empty] | 2020 | May | 14 | 16 | 17940.5 | 28500 | 62.95%
[29 empty] | 2020 | May | 14 | 17 | 8617 | 28500 | 30.24%
[29 empty] | 2020 | May | 14 | 18 | 1162 | 28500 | 4.077%
[29 empty] | 2020 | May | 14 | 19 | 166 | 28500 | 0.5825%
[29 empty] | 2020 | May | 14 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 14 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 14 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 14 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 15 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 15 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 15 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 15 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 15 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 15 | 5 | 1037.5 | 28500 | 3.64%
[29 empty] | 2020 | May | 15 | 6 | 3732 | 28500 | 13.09%
[29 empty] | 2020 | May | 15 | 7 | 14600 | 28500 | 51.23%
[29 empty] | 2020 | May | 15 | 8 | 24627 | 28500 | 86.41%
[29 empty] | 2020 | May | 15 | 9 | 32547 | 28500 | 114.2%
[29 empty] | 2020 | May | 15 | 10 | 38004.5 | 28500 | 133.3%
[29 empty] | 2020 | May | 15 | 11 | 40385 | 28500 | 141.7%
[29 empty] | 2020 | May | 15 | 12 | 41012 | 28500 | 143.9%
[29 empty] | 2020 | May | 15 | 13 | 37837.5 | 28500 | 132.8%
[29 empty] | 2020 | May | 15 | 14 | 33294 | 28500 | 116.8%
[29 empty] | 2020 | May | 15 | 15 | 27357 | 28500 | 95.99%
[29 empty] | 2020 | May | 15 | 16 | 18350 | 28500 | 64.39%
[29 empty] | 2020 | May | 15 | 17 | 8281 | 28500 | 29.06%
[29 empty] | 2020 | May | 15 | 18 | 2017.5 | 28500 | 7.079%
[29 empty] | 2020 | May | 15 | 19 | 55 | 28500 | 0.193%
[29 empty] | 2020 | May | 15 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 15 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 15 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 15 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 16 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 16 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 16 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 16 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 16 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 16 | 5 | 322.5 | 28500 | 1.132%
[29 empty] | 2020 | May | 16 | 6 | 4290.5 | 28500 | 15.05%
[29 empty] | 2020 | May | 16 | 7 | 5031.5 | 28500 | 17.65%
[29 empty] | 2020 | May | 16 | 8 | 14728 | 28500 | 51.68%
[29 empty] | 2020 | May | 16 | 9 | 23419 | 28500 | 82.17%
[29 empty] | 2020 | May | 16 | 10 | 33207 | 28500 | 116.5%
[29 empty] | 2020 | May | 16 | 11 | 21592.5 | 28500 | 75.76%
[29 empty] | 2020 | May | 16 | 12 | 16311 | 28500 | 57.23%
[29 empty] | 2020 | May | 16 | 13 | 17900.5 | 28500 | 62.81%
[29 empty] | 2020 | May | 16 | 14 | 25877 | 28500 | 90.8%
[29 empty] | 2020 | May | 16 | 15 | 21469 | 28500 | 75.33%
[29 empty] | 2020 | May | 16 | 16 | 13910.5 | 28500 | 48.81%
[29 empty] | 2020 | May | 16 | 17 | 7530.5 | 28500 | 26.42%
[29 empty] | 2020 | May | 16 | 18 | 2554.5 | 28500 | 8.963%
[29 empty] | 2020 | May | 16 | 19 | 37 | 28500 | 0.1298%
[29 empty] | 2020 | May | 16 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 16 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 16 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 16 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 17 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 17 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 17 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 17 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 17 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 17 | 5 | 1148.5 | 28500 | 4.03%
[29 empty] | 2020 | May | 17 | 6 | 3840 | 28500 | 13.47%
[29 empty] | 2020 | May | 17 | 7 | 13521.5 | 28500 | 47.44%
[29 empty] | 2020 | May | 17 | 8 | 10116 | 28500 | 35.49%
[29 empty] | 2020 | May | 17 | 9 | 15358.5 | 28500 | 53.89%
[29 empty] | 2020 | May | 17 | 10 | 20833.5 | 28500 | 73.1%
[29 empty] | 2020 | May | 17 | 11 | 31125.5 | 28500 | 109.2%
[29 empty] | 2020 | May | 17 | 12 | 38678 | 28500 | 135.7%
[29 empty] | 2020 | May | 17 | 13 | 33762 | 28500 | 118.5%
[29 empty] | 2020 | May | 17 | 14 | 27345.5 | 28500 | 95.95%
[29 empty] | 2020 | May | 17 | 15 | 25744.5 | 28500 | 90.33%
[29 empty] | 2020 | May | 17 | 16 | 16751 | 28500 | 58.78%
[29 empty] | 2020 | May | 17 | 17 | 8205 | 28500 | 28.79%
[29 empty] | 2020 | May | 17 | 18 | 2481.5 | 28500 | 8.707%
[29 empty] | 2020 | May | 17 | 19 | 54 | 28500 | 0.1895%
[29 empty] | 2020 | May | 17 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 17 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 17 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 17 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 18 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 18 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 18 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 18 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 18 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 18 | 5 | 754 | 28500 | 2.646%
[29 empty] | 2020 | May | 18 | 6 | 4892.5 | 28500 | 17.17%
[29 empty] | 2020 | May | 18 | 7 | 14166 | 28500 | 49.71%
[29 empty] | 2020 | May | 18 | 8 | 24055.5 | 28500 | 84.41%
[29 empty] | 2020 | May | 18 | 9 | 32632 | 28500 | 114.5%
[29 empty] | 2020 | May | 18 | 10 | 38685 | 28500 | 135.7%
[29 empty] | 2020 | May | 18 | 11 | 40879 | 28500 | 143.4%
[29 empty] | 2020 | May | 18 | 12 | 41800.5 | 28500 | 146.7%
[29 empty] | 2020 | May | 18 | 13 | 38083.5 | 28500 | 133.6%
[29 empty] | 2020 | May | 18 | 14 | 24444.5 | 28500 | 85.77%
[29 empty] | 2020 | May | 18 | 15 | 15002.5 | 28500 | 52.64%
[29 empty] | 2020 | May | 18 | 16 | 18335 | 28500 | 64.33%
[29 empty] | 2020 | May | 18 | 17 | 8480 | 28500 | 29.75%
[29 empty] | 2020 | May | 18 | 18 | 1306.5 | 28500 | 4.584%
[29 empty] | 2020 | May | 18 | 19 | 227 | 28500 | 0.7965%
[29 empty] | 2020 | May | 18 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 18 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 18 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 18 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 19 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 19 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 19 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 19 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 19 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 19 | 5 | 1091 | 28500 | 3.828%
[29 empty] | 2020 | May | 19 | 6 | 4766 | 28500 | 16.72%
[29 empty] | 2020 | May | 19 | 7 | 6671 | 28500 | 23.41%
[29 empty] | 2020 | May | 19 | 8 | 23160 | 28500 | 81.26%
[29 empty] | 2020 | May | 19 | 9 | 31169 | 28500 | 109.4%
[29 empty] | 2020 | May | 19 | 10 | 36776.5 | 28500 | 129%
[29 empty] | 2020 | May | 19 | 11 | 39743 | 28500 | 139.4%
[29 empty] | 2020 | May | 19 | 12 | 40031 | 28500 | 140.5%
[29 empty] | 2020 | May | 19 | 13 | 38150 | 28500 | 133.9%
[29 empty] | 2020 | May | 19 | 14 | 33720.5 | 28500 | 118.3%
[29 empty] | 2020 | May | 19 | 15 | 26741.5 | 28500 | 93.83%
[29 empty] | 2020 | May | 19 | 16 | 18246 | 28500 | 64.02%
[29 empty] | 2020 | May | 19 | 17 | 8118.5 | 28500 | 28.49%
[29 empty] | 2020 | May | 19 | 18 | 1424.5 | 28500 | 4.998%
[29 empty] | 2020 | May | 19 | 19 | 372.5 | 28500 | 1.307%
[29 empty] | 2020 | May | 19 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 19 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 19 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 19 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 20 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 20 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 20 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 20 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 20 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 20 | 5 | 1082.5 | 28500 | 3.798%
[29 empty] | 2020 | May | 20 | 6 | 3916.5 | 28500 | 13.74%
[29 empty] | 2020 | May | 20 | 7 | 13530 | 28500 | 47.47%
[29 empty] | 2020 | May | 20 | 8 | 23008 | 28500 | 80.73%
[29 empty] | 2020 | May | 20 | 9 | 30798.5 | 28500 | 108.1%
[29 empty] | 2020 | May | 20 | 10 | 36333 | 28500 | 127.5%
[29 empty] | 2020 | May | 20 | 11 | 37870.5 | 28500 | 132.9%
[29 empty] | 2020 | May | 20 | 12 | 40090 | 28500 | 140.7%
[29 empty] | 2020 | May | 20 | 13 | 38303.5 | 28500 | 134.4%
[29 empty] | 2020 | May | 20 | 14 | 34015 | 28500 | 119.4%
[29 empty] | 2020 | May | 20 | 15 | 27759.5 | 28500 | 97.4%
[29 empty] | 2020 | May | 20 | 16 | 18796.5 | 28500 | 65.95%
[29 empty] | 2020 | May | 20 | 17 | 8332.5 | 28500 | 29.24%
[29 empty] | 2020 | May | 20 | 18 | 1176.5 | 28500 | 4.128%
[29 empty] | 2020 | May | 20 | 19 | 399.5 | 28500 | 1.402%
[29 empty] | 2020 | May | 20 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 20 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 20 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 20 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 21 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 21 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 21 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 21 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 21 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 21 | 5 | 1516 | 28500 | 5.319%
[29 empty] | 2020 | May | 21 | 6 | 4627.5 | 28500 | 16.24%
[29 empty] | 2020 | May | 21 | 7 | 10032.5 | 28500 | 35.2%
[29 empty] | 2020 | May | 21 | 8 | 23224.5 | 28500 | 81.49%
[29 empty] | 2020 | May | 21 | 9 | 30432.5 | 28500 | 106.8%
[29 empty] | 2020 | May | 21 | 10 | 35797 | 28500 | 125.6%
[29 empty] | 2020 | May | 21 | 11 | 38679 | 28500 | 135.7%
[29 empty] | 2020 | May | 21 | 12 | 37448 | 28500 | 131.4%
[29 empty] | 2020 | May | 21 | 13 | 33339 | 28500 | 117%
[29 empty] | 2020 | May | 21 | 14 | 32289 | 28500 | 113.3%
[29 empty] | 2020 | May | 21 | 15 | 24179.5 | 28500 | 84.84%
[29 empty] | 2020 | May | 21 | 16 | 16713 | 28500 | 58.64%
[29 empty] | 2020 | May | 21 | 17 | 8060.5 | 28500 | 28.28%
[29 empty] | 2020 | May | 21 | 18 | 2314.5 | 28500 | 8.121%
[29 empty] | 2020 | May | 21 | 19 | 17 | 28500 | 0.05965%
[29 empty] | 2020 | May | 21 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 21 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 21 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 21 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 22 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 22 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 22 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 22 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 22 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 22 | 5 | 466 | 28500 | 1.635%
[29 empty] | 2020 | May | 22 | 6 | 2960 | 28500 | 10.39%
[29 empty] | 2020 | May | 22 | 7 | 7969 | 28500 | 27.96%
[29 empty] | 2020 | May | 22 | 8 | 13057.5 | 28500 | 45.82%
[29 empty] | 2020 | May | 22 | 9 | 15694.5 | 28500 | 55.07%
[29 empty] | 2020 | May | 22 | 10 | 18244.5 | 28500 | 64.02%
[29 empty] | 2020 | May | 22 | 11 | 41279.5 | 28500 | 144.8%
[29 empty] | 2020 | May | 22 | 12 | 41669 | 28500 | 146.2%
[29 empty] | 2020 | May | 22 | 13 | 40138.5 | 28500 | 140.8%
[29 empty] | 2020 | May | 22 | 14 | 35309 | 28500 | 123.9%
[29 empty] | 2020 | May | 22 | 15 | 26638 | 28500 | 93.47%
[29 empty] | 2020 | May | 22 | 16 | 14474.5 | 28500 | 50.79%
[29 empty] | 2020 | May | 22 | 17 | 8663 | 28500 | 30.4%
[29 empty] | 2020 | May | 22 | 18 | 2730.5 | 28500 | 9.581%
[29 empty] | 2020 | May | 22 | 19 | 182 | 28500 | 0.6386%
[29 empty] | 2020 | May | 22 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 22 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 22 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 22 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 23 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 23 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 23 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 23 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 23 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 23 | 5 | 1219.5 | 28500 | 4.279%
[29 empty] | 2020 | May | 23 | 6 | 4066.5 | 28500 | 14.27%
[29 empty] | 2020 | May | 23 | 7 | 12055.5 | 28500 | 42.3%
[29 empty] | 2020 | May | 23 | 8 | 21580.5 | 28500 | 75.72%
[29 empty] | 2020 | May | 23 | 9 | 26524 | 28500 | 93.07%
[29 empty] | 2020 | May | 23 | 10 | 26596 | 28500 | 93.32%
[29 empty] | 2020 | May | 23 | 11 | 41943 | 28500 | 147.2%
[29 empty] | 2020 | May | 23 | 12 | 41506 | 28500 | 145.6%
[29 empty] | 2020 | May | 23 | 13 | 29601 | 28500 | 103.9%
[29 empty] | 2020 | May | 23 | 14 | 25546 | 28500 | 89.64%
[29 empty] | 2020 | May | 23 | 15 | 10086 | 28500 | 35.39%
[29 empty] | 2020 | May | 23 | 16 | 11446 | 28500 | 40.16%
[29 empty] | 2020 | May | 23 | 17 | 8843 | 28500 | 31.03%
[29 empty] | 2020 | May | 23 | 18 | 2842.5 | 28500 | 9.974%
[29 empty] | 2020 | May | 23 | 19 | 497 | 28500 | 1.744%
[29 empty] | 2020 | May | 23 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 23 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 23 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 23 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 24 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 24 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 24 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 24 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 24 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 24 | 5 | 1092 | 28500 | 3.832%
[29 empty] | 2020 | May | 24 | 6 | 4842.5 | 28500 | 16.99%
[29 empty] | 2020 | May | 24 | 7 | 12629.5 | 28500 | 44.31%
[29 empty] | 2020 | May | 24 | 8 | 7577.5 | 28500 | 26.59%
[29 empty] | 2020 | May | 24 | 9 | 20976.5 | 28500 | 73.6%
[29 empty] | 2020 | May | 24 | 10 | 22088.5 | 28500 | 77.5%
[29 empty] | 2020 | May | 24 | 11 | 32460.5 | 28500 | 113.9%
[29 empty] | 2020 | May | 24 | 12 | 19447.5 | 28500 | 68.24%
[29 empty] | 2020 | May | 24 | 13 | 23889 | 28500 | 83.82%
[29 empty] | 2020 | May | 24 | 14 | 24521 | 28500 | 86.04%
[29 empty] | 2020 | May | 24 | 15 | 12595.5 | 28500 | 44.19%
[29 empty] | 2020 | May | 24 | 16 | 8245.5 | 28500 | 28.93%
[29 empty] | 2020 | May | 24 | 17 | 5701 | 28500 | 20%
[29 empty] | 2020 | May | 24 | 18 | 2660 | 28500 | 9.333%
[29 empty] | 2020 | May | 24 | 19 | 487 | 28500 | 1.709%
[29 empty] | 2020 | May | 24 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 24 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 24 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 24 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 25 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 25 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 25 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 25 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 25 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 25 | 5 | 1323 | 28500 | 4.642%
[29 empty] | 2020 | May | 25 | 6 | 4138.5 | 28500 | 14.52%
[29 empty] | 2020 | May | 25 | 7 | 13893 | 28500 | 48.75%
[29 empty] | 2020 | May | 25 | 8 | 23407 | 28500 | 82.13%
[29 empty] | 2020 | May | 25 | 9 | 30328 | 28500 | 106.4%
[29 empty] | 2020 | May | 25 | 10 | 32147.5 | 28500 | 112.8%
[29 empty] | 2020 | May | 25 | 11 | 37040 | 28500 | 130%
[29 empty] | 2020 | May | 25 | 12 | 37639 | 28500 | 132.1%
[29 empty] | 2020 | May | 25 | 13 | 31156 | 28500 | 109.3%
[29 empty] | 2020 | May | 25 | 14 | 25299 | 28500 | 88.77%
[29 empty] | 2020 | May | 25 | 15 | 22307.5 | 28500 | 78.27%
[29 empty] | 2020 | May | 25 | 16 | 15790 | 28500 | 55.4%
[29 empty] | 2020 | May | 25 | 17 | 8570.5 | 28500 | 30.07%
[29 empty] | 2020 | May | 25 | 18 | 1067.5 | 28500 | 3.746%
[29 empty] | 2020 | May | 25 | 19 | 593 | 28500 | 2.081%
[29 empty] | 2020 | May | 25 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 25 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 25 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 25 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 26 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 26 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 26 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 26 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 26 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 26 | 5 | 1218 | 28500 | 4.274%
[29 empty] | 2020 | May | 26 | 6 | 4086.5 | 28500 | 14.34%
[29 empty] | 2020 | May | 26 | 7 | 13378 | 28500 | 46.94%
[29 empty] | 2020 | May | 26 | 8 | 22224 | 28500 | 77.98%
[29 empty] | 2020 | May | 26 | 9 | 29714.5 | 28500 | 104.3%
[29 empty] | 2020 | May | 26 | 10 | 34649.5 | 28500 | 121.6%
[29 empty] | 2020 | May | 26 | 11 | 37818.5 | 28500 | 132.7%
[29 empty] | 2020 | May | 26 | 12 | 35752.5 | 28500 | 125.4%
[29 empty] | 2020 | May | 26 | 13 | 34349 | 28500 | 120.5%
[29 empty] | 2020 | May | 26 | 14 | 31884 | 28500 | 111.9%
[29 empty] | 2020 | May | 26 | 15 | 21517.5 | 28500 | 75.5%
[29 empty] | 2020 | May | 26 | 16 | 12847.5 | 28500 | 45.08%
[29 empty] | 2020 | May | 26 | 17 | 6858 | 28500 | 24.06%
[29 empty] | 2020 | May | 26 | 18 | 2251 | 28500 | 7.898%
[29 empty] | 2020 | May | 26 | 19 | 642 | 28500 | 2.253%
[29 empty] | 2020 | May | 26 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 26 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 26 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 26 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 27 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 27 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 27 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 27 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 27 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 27 | 5 | 1428.5 | 28500 | 5.012%
[29 empty] | 2020 | May | 27 | 6 | 4322 | 28500 | 15.16%
[29 empty] | 2020 | May | 27 | 7 | 13176 | 28500 | 46.23%
[29 empty] | 2020 | May | 27 | 8 | 22349.5 | 28500 | 78.42%
[29 empty] | 2020 | May | 27 | 9 | 29119.5 | 28500 | 102.2%
[29 empty] | 2020 | May | 27 | 10 | 33490 | 28500 | 117.5%
[29 empty] | 2020 | May | 27 | 11 | 32711.5 | 28500 | 114.8%
[29 empty] | 2020 | May | 27 | 12 | 15019.5 | 28500 | 52.7%
[29 empty] | 2020 | May | 27 | 13 | 14275 | 28500 | 50.09%
[29 empty] | 2020 | May | 27 | 14 | 27485.5 | 28500 | 96.44%
[29 empty] | 2020 | May | 27 | 15 | 23592 | 28500 | 82.78%
[29 empty] | 2020 | May | 27 | 16 | 16039 | 28500 | 56.28%
[29 empty] | 2020 | May | 27 | 17 | 8266 | 28500 | 29%
[29 empty] | 2020 | May | 27 | 18 | 2614 | 28500 | 9.172%
[29 empty] | 2020 | May | 27 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 27 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 27 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 27 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 27 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 28 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 28 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 28 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 28 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 28 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 28 | 5 | 1184 | 28500 | 4.154%
[29 empty] | 2020 | May | 28 | 6 | 4633.5 | 28500 | 16.26%
[29 empty] | 2020 | May | 28 | 7 | 12323.5 | 28500 | 43.24%
[29 empty] | 2020 | May | 28 | 8 | 23812 | 28500 | 83.55%
[29 empty] | 2020 | May | 28 | 9 | 31984 | 28500 | 112.2%
[29 empty] | 2020 | May | 28 | 10 | 37757 | 28500 | 132.5%
[29 empty] | 2020 | May | 28 | 11 | 41323 | 28500 | 145%
[29 empty] | 2020 | May | 28 | 12 | 41690 | 28500 | 146.3%
[29 empty] | 2020 | May | 28 | 13 | 40147.5 | 28500 | 140.9%
[29 empty] | 2020 | May | 28 | 14 | 35247 | 28500 | 123.7%
[29 empty] | 2020 | May | 28 | 15 | 28715 | 28500 | 100.8%
[29 empty] | 2020 | May | 28 | 16 | 19342.5 | 28500 | 67.87%
[29 empty] | 2020 | May | 28 | 17 | 8992 | 28500 | 31.55%
[29 empty] | 2020 | May | 28 | 18 | 1594.5 | 28500 | 5.595%
[29 empty] | 2020 | May | 28 | 19 | 610 | 28500 | 2.14%
[29 empty] | 2020 | May | 28 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 28 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 28 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 28 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 29 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 29 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 29 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 29 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 29 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 29 | 5 | 1381.5 | 28500 | 4.847%
[29 empty] | 2020 | May | 29 | 6 | 4049.5 | 28500 | 14.21%
[29 empty] | 2020 | May | 29 | 7 | 14242 | 28500 | 49.97%
[29 empty] | 2020 | May | 29 | 8 | 24018 | 28500 | 84.27%
[29 empty] | 2020 | May | 29 | 9 | 31712.5 | 28500 | 111.3%
[29 empty] | 2020 | May | 29 | 10 | 37272 | 28500 | 130.8%
[29 empty] | 2020 | May | 29 | 11 | 41006 | 28500 | 143.9%
[29 empty] | 2020 | May | 29 | 12 | 41622.5 | 28500 | 146%
[29 empty] | 2020 | May | 29 | 13 | 39968 | 28500 | 140.2%
[29 empty] | 2020 | May | 29 | 14 | 35369.5 | 28500 | 124.1%
[29 empty] | 2020 | May | 29 | 15 | 28540 | 28500 | 100.1%
[29 empty] | 2020 | May | 29 | 16 | 19435 | 28500 | 68.19%
[29 empty] | 2020 | May | 29 | 17 | 9025 | 28500 | 31.67%
[29 empty] | 2020 | May | 29 | 18 | 1326 | 28500 | 4.653%
[29 empty] | 2020 | May | 29 | 19 | 580.5 | 28500 | 2.037%
[29 empty] | 2020 | May | 29 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 29 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 29 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 29 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 30 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 30 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 30 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 30 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 30 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 30 | 5 | 1649.5 | 28500 | 5.788%
[29 empty] | 2020 | May | 30 | 6 | 5234 | 28500 | 18.36%
[29 empty] | 2020 | May | 30 | 7 | 13946.5 | 28500 | 48.94%
[29 empty] | 2020 | May | 30 | 8 | 23898.5 | 28500 | 83.85%
[29 empty] | 2020 | May | 30 | 9 | 31663 | 28500 | 111.1%
[29 empty] | 2020 | May | 30 | 10 | 37393 | 28500 | 131.2%
[29 empty] | 2020 | May | 30 | 11 | 40845.5 | 28500 | 143.3%
[29 empty] | 2020 | May | 30 | 12 | 41988 | 28500 | 147.3%
[29 empty] | 2020 | May | 30 | 13 | 40106 | 28500 | 140.7%
[29 empty] | 2020 | May | 30 | 14 | 35470 | 28500 | 124.5%
[29 empty] | 2020 | May | 30 | 15 | 28770.5 | 28500 | 100.9%
[29 empty] | 2020 | May | 30 | 16 | 19445.5 | 28500 | 68.23%
[29 empty] | 2020 | May | 30 | 17 | 9047.5 | 28500 | 31.75%
[29 empty] | 2020 | May | 30 | 18 | 1467 | 28500 | 5.147%
[29 empty] | 2020 | May | 30 | 19 | 687 | 28500 | 2.411%
[29 empty] | 2020 | May | 30 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 30 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 30 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 30 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 31 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 31 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 31 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 31 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 31 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 31 | 5 | 1533 | 28500 | 5.379%
[29 empty] | 2020 | May | 31 | 6 | 4269 | 28500 | 14.98%
[29 empty] | 2020 | May | 31 | 7 | 13954 | 28500 | 48.96%
[29 empty] | 2020 | May | 31 | 8 | 23454.5 | 28500 | 82.3%
[29 empty] | 2020 | May | 31 | 9 | 31092.5 | 28500 | 109.1%
[29 empty] | 2020 | May | 31 | 10 | 36254.5 | 28500 | 127.2%
[29 empty] | 2020 | May | 31 | 11 | 38818.5 | 28500 | 136.2%
[29 empty] | 2020 | May | 31 | 12 | 41521.5 | 28500 | 145.7%
[29 empty] | 2020 | May | 31 | 13 | 39790.5 | 28500 | 139.6%
[29 empty] | 2020 | May | 31 | 14 | 35633.5 | 28500 | 125%
[29 empty] | 2020 | May | 31 | 15 | 28476.5 | 28500 | 99.92%
[29 empty] | 2020 | May | 31 | 16 | 19487.5 | 28500 | 68.38%
[29 empty] | 2020 | May | 31 | 17 | 9125 | 28500 | 32.02%
[29 empty] | 2020 | May | 31 | 18 | 1444.5 | 28500 | 5.068%
[29 empty] | 2020 | May | 31 | 19 | 604.5 | 28500 | 2.121%
[29 empty] | 2020 | May | 31 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 31 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 31 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | May | 31 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 1 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 1 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 1 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 1 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 1 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 1 | 5 | 1307 | 28500 | 4.586%
[29 empty] | 2020 | June | 1 | 6 | 4204.5 | 28500 | 14.75%
[29 empty] | 2020 | June | 1 | 7 | 13801.5 | 28500 | 48.43%
[29 empty] | 2020 | June | 1 | 8 | 23405 | 28500 | 82.12%
[29 empty] | 2020 | June | 1 | 9 | 30894 | 28500 | 108.4%
[29 empty] | 2020 | June | 1 | 10 | 36626.5 | 28500 | 128.5%
[29 empty] | 2020 | June | 1 | 11 | 40216.5 | 28500 | 141.1%
[29 empty] | 2020 | June | 1 | 12 | 40772.5 | 28500 | 143.1%
[29 empty] | 2020 | June | 1 | 13 | 38851.5 | 28500 | 136.3%
[29 empty] | 2020 | June | 1 | 14 | 34492.5 | 28500 | 121%
[29 empty] | 2020 | June | 1 | 15 | 27802.5 | 28500 | 97.55%
[29 empty] | 2020 | June | 1 | 16 | 18938 | 28500 | 66.45%
[29 empty] | 2020 | June | 1 | 17 | 8948 | 28500 | 31.4%
[29 empty] | 2020 | June | 1 | 18 | 1516.5 | 28500 | 5.321%
[29 empty] | 2020 | June | 1 | 19 | 712 | 28500 | 2.498%
[29 empty] | 2020 | June | 1 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 1 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 1 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 1 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 2 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 2 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 2 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 2 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 2 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 2 | 5 | 1381 | 28500 | 4.846%
[29 empty] | 2020 | June | 2 | 6 | 4612.5 | 28500 | 16.18%
[29 empty] | 2020 | June | 2 | 7 | 13641 | 28500 | 47.86%
[29 empty] | 2020 | June | 2 | 8 | 23843 | 28500 | 83.66%
[29 empty] | 2020 | June | 2 | 9 | 30930.5 | 28500 | 108.5%
[29 empty] | 2020 | June | 2 | 10 | 36116 | 28500 | 126.7%
[29 empty] | 2020 | June | 2 | 11 | 39135.5 | 28500 | 137.3%
[29 empty] | 2020 | June | 2 | 12 | 39506 | 28500 | 138.6%
[29 empty] | 2020 | June | 2 | 13 | 37766.5 | 28500 | 132.5%
[29 empty] | 2020 | June | 2 | 14 | 33920 | 28500 | 119%
[29 empty] | 2020 | June | 2 | 15 | 20691 | 28500 | 72.6%
[29 empty] | 2020 | June | 2 | 16 | 14255 | 28500 | 50.02%
[29 empty] | 2020 | June | 2 | 17 | 8833.5 | 28500 | 30.99%
[29 empty] | 2020 | June | 2 | 18 | 1566 | 28500 | 5.495%
[29 empty] | 2020 | June | 2 | 19 | 761.5 | 28500 | 2.672%
[29 empty] | 2020 | June | 2 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 2 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 2 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 2 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 3 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 3 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 3 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 3 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 3 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 3 | 5 | 258 | 28500 | 0.9053%
[29 empty] | 2020 | June | 3 | 6 | 2436 | 28500 | 8.547%
[29 empty] | 2020 | June | 3 | 7 | 8498.5 | 28500 | 29.82%
[29 empty] | 2020 | June | 3 | 8 | 6029.5 | 28500 | 21.16%
[29 empty] | 2020 | June | 3 | 9 | 7796 | 28500 | 27.35%
[29 empty] | 2020 | June | 3 | 10 | 10890.5 | 28500 | 38.21%
[29 empty] | 2020 | June | 3 | 11 | 18204.5 | 28500 | 63.88%
[29 empty] | 2020 | June | 3 | 12 | 24072 | 28500 | 84.46%
[29 empty] | 2020 | June | 3 | 13 | 9944.5 | 28500 | 34.89%
[29 empty] | 2020 | June | 3 | 14 | 8832.5 | 28500 | 30.99%
[29 empty] | 2020 | June | 3 | 15 | 3394.5 | 28500 | 11.91%
[29 empty] | 2020 | June | 3 | 16 | 4687.5 | 28500 | 16.45%
[29 empty] | 2020 | June | 3 | 17 | 5461.5 | 28500 | 19.16%
[29 empty] | 2020 | June | 3 | 18 | 838.5 | 28500 | 2.942%
[29 empty] | 2020 | June | 3 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 3 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 3 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 3 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 3 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 4 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 4 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 4 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 4 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 4 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 4 | 5 | 453.5 | 28500 | 1.591%
[29 empty] | 2020 | June | 4 | 6 | 2534 | 28500 | 8.891%
[29 empty] | 2020 | June | 4 | 7 | 1964 | 28500 | 6.891%
[29 empty] | 2020 | June | 4 | 8 | 3543.5 | 28500 | 12.43%
[29 empty] | 2020 | June | 4 | 9 | 9402 | 28500 | 32.99%
[29 empty] | 2020 | June | 4 | 10 | 9353.5 | 28500 | 32.82%
[29 empty] | 2020 | June | 4 | 11 | 15920 | 28500 | 55.86%
[29 empty] | 2020 | June | 4 | 12 | 35429.5 | 28500 | 124.3%
[29 empty] | 2020 | June | 4 | 13 | 21481 | 28500 | 75.37%
[29 empty] | 2020 | June | 4 | 14 | 5033.5 | 28500 | 17.66%
[29 empty] | 2020 | June | 4 | 15 | 12516.5 | 28500 | 43.92%
[29 empty] | 2020 | June | 4 | 16 | 3863 | 28500 | 13.55%
[29 empty] | 2020 | June | 4 | 17 | 3806 | 28500 | 13.35%
[29 empty] | 2020 | June | 4 | 18 | 985.5 | 28500 | 3.458%
[29 empty] | 2020 | June | 4 | 19 | 798.5 | 28500 | 2.802%
[29 empty] | 2020 | June | 4 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 4 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 4 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 4 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 5 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 5 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 5 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 5 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 5 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 5 | 5 | 1757.5 | 28500 | 6.167%
[29 empty] | 2020 | June | 5 | 6 | 5386 | 28500 | 18.9%
[29 empty] | 2020 | June | 5 | 7 | 10329.5 | 28500 | 36.24%
[29 empty] | 2020 | June | 5 | 8 | 6922 | 28500 | 24.29%
[29 empty] | 2020 | June | 5 | 9 | 3931.5 | 28500 | 13.79%
[29 empty] | 2020 | June | 5 | 10 | 7893.5 | 28500 | 27.7%
[29 empty] | 2020 | June | 5 | 11 | 32881 | 28500 | 115.4%
[29 empty] | 2020 | June | 5 | 12 | 6260 | 28500 | 21.96%
[29 empty] | 2020 | June | 5 | 13 | 19894.5 | 28500 | 69.81%
[29 empty] | 2020 | June | 5 | 14 | 33410.5 | 28500 | 117.2%
[29 empty] | 2020 | June | 5 | 15 | 27924 | 28500 | 97.98%
[29 empty] | 2020 | June | 5 | 16 | 5977 | 28500 | 20.97%
[29 empty] | 2020 | June | 5 | 17 | 4668 | 28500 | 16.38%
[29 empty] | 2020 | June | 5 | 18 | 3432 | 28500 | 12.04%
[29 empty] | 2020 | June | 5 | 19 | 735 | 28500 | 2.579%
[29 empty] | 2020 | June | 5 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 5 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 5 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 5 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 6 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 6 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 6 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 6 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 6 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 6 | 5 | 1271.5 | 28500 | 4.461%
[29 empty] | 2020 | June | 6 | 6 | 4020.5 | 28500 | 14.11%
[29 empty] | 2020 | June | 6 | 7 | 14492.5 | 28500 | 50.85%
[29 empty] | 2020 | June | 6 | 8 | 22903.5 | 28500 | 80.36%
[29 empty] | 2020 | June | 6 | 9 | 19494 | 28500 | 68.4%
[29 empty] | 2020 | June | 6 | 10 | 16033 | 28500 | 56.26%
[29 empty] | 2020 | June | 6 | 11 | 8287.5 | 28500 | 29.08%
[29 empty] | 2020 | June | 6 | 12 | 8411 | 28500 | 29.51%
[29 empty] | 2020 | June | 6 | 13 | 9219 | 28500 | 32.35%
[29 empty] | 2020 | June | 6 | 14 | 13014.5 | 28500 | 45.66%
[29 empty] | 2020 | June | 6 | 15 | 6655.5 | 28500 | 23.35%
[29 empty] | 2020 | June | 6 | 16 | 2947.5 | 28500 | 10.34%
[29 empty] | 2020 | June | 6 | 17 | 2715 | 28500 | 9.526%
[29 empty] | 2020 | June | 6 | 18 | 591.5 | 28500 | 2.075%
[29 empty] | 2020 | June | 6 | 19 | 4 | 28500 | 0.01404%
[29 empty] | 2020 | June | 6 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 6 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 6 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 6 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 7 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 7 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 7 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 7 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 7 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 7 | 5 | 2016 | 28500 | 7.074%
[29 empty] | 2020 | June | 7 | 6 | 5347.5 | 28500 | 18.76%
[29 empty] | 2020 | June | 7 | 7 | 13219.5 | 28500 | 46.38%
[29 empty] | 2020 | June | 7 | 8 | 23370.5 | 28500 | 82%
[29 empty] | 2020 | June | 7 | 9 | 28351.5 | 28500 | 99.48%
[29 empty] | 2020 | June | 7 | 10 | 23035.5 | 28500 | 80.83%
[29 empty] | 2020 | June | 7 | 11 | 35099.5 | 28500 | 123.2%
[29 empty] | 2020 | June | 7 | 12 | 26570.5 | 28500 | 93.23%
[29 empty] | 2020 | June | 7 | 13 | 14932.5 | 28500 | 52.39%
[29 empty] | 2020 | June | 7 | 14 | 6920.5 | 28500 | 24.28%
[29 empty] | 2020 | June | 7 | 15 | 4704.5 | 28500 | 16.51%
[29 empty] | 2020 | June | 7 | 16 | 4915.5 | 28500 | 17.25%
[29 empty] | 2020 | June | 7 | 17 | 2781.5 | 28500 | 9.76%
[29 empty] | 2020 | June | 7 | 18 | 351 | 28500 | 1.232%
[29 empty] | 2020 | June | 7 | 19 | 921 | 28500 | 3.232%
[29 empty] | 2020 | June | 7 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 7 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 7 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 7 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 8 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 8 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 8 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 8 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 8 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 8 | 5 | 1597 | 28500 | 5.604%
[29 empty] | 2020 | June | 8 | 6 | 5388.5 | 28500 | 18.91%
[29 empty] | 2020 | June | 8 | 7 | 8403.5 | 28500 | 29.49%
[29 empty] | 2020 | June | 8 | 8 | 11997.5 | 28500 | 42.1%
[29 empty] | 2020 | June | 8 | 9 | 17035.5 | 28500 | 59.77%
[29 empty] | 2020 | June | 8 | 10 | 17698.5 | 28500 | 62.1%
[29 empty] | 2020 | June | 8 | 11 | 10884.5 | 28500 | 38.19%
[29 empty] | 2020 | June | 8 | 12 | 12224 | 28500 | 42.89%
[29 empty] | 2020 | June | 8 | 13 | 14188.5 | 28500 | 49.78%
[29 empty] | 2020 | June | 8 | 14 | 9062.5 | 28500 | 31.8%
[29 empty] | 2020 | June | 8 | 15 | 11854.5 | 28500 | 41.59%
[29 empty] | 2020 | June | 8 | 16 | 9067 | 28500 | 31.81%
[29 empty] | 2020 | June | 8 | 17 | 7738.5 | 28500 | 27.15%
[29 empty] | 2020 | June | 8 | 18 | 3159.5 | 28500 | 11.09%
[29 empty] | 2020 | June | 8 | 19 | 1010 | 28500 | 3.544%
[29 empty] | 2020 | June | 8 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 8 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 8 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 8 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 9 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 9 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 9 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 9 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 9 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 9 | 5 | 1521 | 28500 | 5.337%
[29 empty] | 2020 | June | 9 | 6 | 5323 | 28500 | 18.68%
[29 empty] | 2020 | June | 9 | 7 | 10161 | 28500 | 35.65%
[29 empty] | 2020 | June | 9 | 8 | 21047 | 28500 | 73.85%
[29 empty] | 2020 | June | 9 | 9 | 29361.5 | 28500 | 103%
[29 empty] | 2020 | June | 9 | 10 | 36477 | 28500 | 128%
[29 empty] | 2020 | June | 9 | 11 | 33853.5 | 28500 | 118.8%
[29 empty] | 2020 | June | 9 | 12 | 11850.5 | 28500 | 41.58%
[29 empty] | 2020 | June | 9 | 13 | 24444 | 28500 | 85.77%
[29 empty] | 2020 | June | 9 | 14 | 23359 | 28500 | 81.96%
[29 empty] | 2020 | June | 9 | 15 | 18332 | 28500 | 64.32%
[29 empty] | 2020 | June | 9 | 16 | 12584 | 28500 | 44.15%
[29 empty] | 2020 | June | 9 | 17 | 7466.5 | 28500 | 26.2%
[29 empty] | 2020 | June | 9 | 18 | 1207.5 | 28500 | 4.237%
[29 empty] | 2020 | June | 9 | 19 | 998.5 | 28500 | 3.504%
[29 empty] | 2020 | June | 9 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 9 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 9 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 9 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 10 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 10 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 10 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 10 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 10 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 10 | 5 | 140.5 | 28500 | 0.493%
[29 empty] | 2020 | June | 10 | 6 | 922.5 | 28500 | 3.237%
[29 empty] | 2020 | June | 10 | 7 | 2950.5 | 28500 | 10.35%
[29 empty] | 2020 | June | 10 | 8 | 5678.5 | 28500 | 19.92%
[29 empty] | 2020 | June | 10 | 9 | 4277.5 | 28500 | 15.01%
[29 empty] | 2020 | June | 10 | 10 | 5613.5 | 28500 | 19.7%
[29 empty] | 2020 | June | 10 | 11 | 6955.5 | 28500 | 24.41%
[29 empty] | 2020 | June | 10 | 12 | 4014 | 28500 | 14.08%
[29 empty] | 2020 | June | 10 | 13 | 5401.5 | 28500 | 18.95%
[29 empty] | 2020 | June | 10 | 14 | 9288 | 28500 | 32.59%
[29 empty] | 2020 | June | 10 | 15 | 5407.5 | 28500 | 18.97%
[29 empty] | 2020 | June | 10 | 16 | 3570.5 | 28500 | 12.53%
[29 empty] | 2020 | June | 10 | 17 | 4178 | 28500 | 14.66%
[29 empty] | 2020 | June | 10 | 18 | 2449 | 28500 | 8.593%
[29 empty] | 2020 | June | 10 | 19 | 707 | 28500 | 2.481%
[29 empty] | 2020 | June | 10 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 10 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 10 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 10 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 11 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 11 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 11 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 11 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 11 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 11 | 5 | 1987 | 28500 | 6.972%
[29 empty] | 2020 | June | 11 | 6 | 4972.5 | 28500 | 17.45%
[29 empty] | 2020 | June | 11 | 7 | 2381 | 28500 | 8.354%
[29 empty] | 2020 | June | 11 | 8 | 9851 | 28500 | 34.56%
[29 empty] | 2020 | June | 11 | 9 | 4197.5 | 28500 | 14.73%
[29 empty] | 2020 | June | 11 | 10 | 2307.5 | 28500 | 8.096%
[29 empty] | 2020 | June | 11 | 11 | 3668.5 | 28500 | 12.87%
[29 empty] | 2020 | June | 11 | 12 | 4779 | 28500 | 16.77%
[29 empty] | 2020 | June | 11 | 13 | 26618 | 28500 | 93.4%
[29 empty] | 2020 | June | 11 | 14 | 30536.5 | 28500 | 107.1%
[29 empty] | 2020 | June | 11 | 15 | 16146 | 28500 | 56.65%
[29 empty] | 2020 | June | 11 | 16 | 5984.5 | 28500 | 21%
[29 empty] | 2020 | June | 11 | 17 | 6266 | 28500 | 21.99%
[29 empty] | 2020 | June | 11 | 18 | 1174.5 | 28500 | 4.121%
[29 empty] | 2020 | June | 11 | 19 | 116 | 28500 | 0.407%
[29 empty] | 2020 | June | 11 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 11 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 11 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 11 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 12 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 12 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 12 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 12 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 12 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 12 | 5 | 1902 | 28500 | 6.674%
[29 empty] | 2020 | June | 12 | 6 | 4296 | 28500 | 15.07%
[29 empty] | 2020 | June | 12 | 7 | 6615.5 | 28500 | 23.21%
[29 empty] | 2020 | June | 12 | 8 | 15172.5 | 28500 | 53.24%
[29 empty] | 2020 | June | 12 | 9 | 19143 | 28500 | 67.17%
[29 empty] | 2020 | June | 12 | 10 | 15421.5 | 28500 | 54.11%
[29 empty] | 2020 | June | 12 | 11 | 5394 | 28500 | 18.93%
[29 empty] | 2020 | June | 12 | 12 | 5597 | 28500 | 19.64%
[29 empty] | 2020 | June | 12 | 13 | 7678.5 | 28500 | 26.94%
[29 empty] | 2020 | June | 12 | 14 | 3603 | 28500 | 12.64%
[29 empty] | 2020 | June | 12 | 15 | 3159 | 28500 | 11.08%
[29 empty] | 2020 | June | 12 | 16 | 3720 | 28500 | 13.05%
[29 empty] | 2020 | June | 12 | 17 | 2748.5 | 28500 | 9.644%
[29 empty] | 2020 | June | 12 | 18 | 3119 | 28500 | 10.94%
[29 empty] | 2020 | June | 12 | 19 | 93.5 | 28500 | 0.3281%
[29 empty] | 2020 | June | 12 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 12 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 12 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 12 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 13 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 13 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 13 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 13 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 13 | 4 | 117.5 | 28500 | 0.4123%
[29 empty] | 2020 | June | 13 | 5 | 1862.5 | 28500 | 6.535%
[29 empty] | 2020 | June | 13 | 6 | 1531.5 | 28500 | 5.374%
[29 empty] | 2020 | June | 13 | 7 | 13155 | 28500 | 46.16%
[29 empty] | 2020 | June | 13 | 8 | 17915 | 28500 | 62.86%
[29 empty] | 2020 | June | 13 | 9 | 29880 | 28500 | 104.8%
[29 empty] | 2020 | June | 13 | 10 | 36393.5 | 28500 | 127.7%
[29 empty] | 2020 | June | 13 | 11 | 39548.5 | 28500 | 138.8%
[29 empty] | 2020 | June | 13 | 12 | 30489 | 28500 | 107%
[29 empty] | 2020 | June | 13 | 13 | 32220 | 28500 | 113.1%
[29 empty] | 2020 | June | 13 | 14 | 10131.5 | 28500 | 35.55%
[29 empty] | 2020 | June | 13 | 15 | 16928 | 28500 | 59.4%
[29 empty] | 2020 | June | 13 | 16 | 16621.5 | 28500 | 58.32%
[29 empty] | 2020 | June | 13 | 17 | 5268 | 28500 | 18.48%
[29 empty] | 2020 | June | 13 | 18 | 1638.5 | 28500 | 5.749%
[29 empty] | 2020 | June | 13 | 19 | 773.5 | 28500 | 2.714%
[29 empty] | 2020 | June | 13 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 13 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 13 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 13 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 14 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 14 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 14 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 14 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 14 | 4 | 140 | 28500 | 0.4912%
[29 empty] | 2020 | June | 14 | 5 | 1366.5 | 28500 | 4.795%
[29 empty] | 2020 | June | 14 | 6 | 4050 | 28500 | 14.21%
[29 empty] | 2020 | June | 14 | 7 | 12963 | 28500 | 45.48%
[29 empty] | 2020 | June | 14 | 8 | 16748 | 28500 | 58.76%
[29 empty] | 2020 | June | 14 | 9 | 18197.5 | 28500 | 63.85%
[29 empty] | 2020 | June | 14 | 10 | 30323 | 28500 | 106.4%
[29 empty] | 2020 | June | 14 | 11 | 18748 | 28500 | 65.78%
[29 empty] | 2020 | June | 14 | 12 | 23516 | 28500 | 82.51%
[29 empty] | 2020 | June | 14 | 13 | 14449.5 | 28500 | 50.7%
[29 empty] | 2020 | June | 14 | 14 | 8942.5 | 28500 | 31.38%
[29 empty] | 2020 | June | 14 | 15 | 14101 | 28500 | 49.48%
[29 empty] | 2020 | June | 14 | 16 | 12101.5 | 28500 | 42.46%
[29 empty] | 2020 | June | 14 | 17 | 9100.5 | 28500 | 31.93%
[29 empty] | 2020 | June | 14 | 18 | 2542.5 | 28500 | 8.921%
[29 empty] | 2020 | June | 14 | 19 | 1138.5 | 28500 | 3.995%
[29 empty] | 2020 | June | 14 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 14 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 14 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 14 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 15 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 15 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 15 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 15 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 15 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 15 | 5 | 1439.5 | 28500 | 5.051%
[29 empty] | 2020 | June | 15 | 6 | 3941 | 28500 | 13.83%
[29 empty] | 2020 | June | 15 | 7 | 13288.5 | 28500 | 46.63%
[29 empty] | 2020 | June | 15 | 8 | 22445.5 | 28500 | 78.76%
[29 empty] | 2020 | June | 15 | 9 | 29590.5 | 28500 | 103.8%
[29 empty] | 2020 | June | 15 | 10 | 28314 | 28500 | 99.35%
[29 empty] | 2020 | June | 15 | 11 | 17135.5 | 28500 | 60.12%
[29 empty] | 2020 | June | 15 | 12 | 4579.5 | 28500 | 16.07%
[29 empty] | 2020 | June | 15 | 13 | 6924.5 | 28500 | 24.3%
[29 empty] | 2020 | June | 15 | 14 | 5932.5 | 28500 | 20.82%
[29 empty] | 2020 | June | 15 | 15 | 2925 | 28500 | 10.26%
[29 empty] | 2020 | June | 15 | 16 | 5845.5 | 28500 | 20.51%
[29 empty] | 2020 | June | 15 | 17 | 8688 | 28500 | 30.48%
[29 empty] | 2020 | June | 15 | 18 | 2599.5 | 28500 | 9.121%
[29 empty] | 2020 | June | 15 | 19 | 1071.5 | 28500 | 3.76%
[29 empty] | 2020 | June | 15 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 15 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 15 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 15 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 16 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 16 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 16 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 16 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 16 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 16 | 5 | 1969.5 | 28500 | 6.911%
[29 empty] | 2020 | June | 16 | 6 | 4864 | 28500 | 17.07%
[29 empty] | 2020 | June | 16 | 7 | 13199 | 28500 | 46.31%
[29 empty] | 2020 | June | 16 | 8 | 20181.5 | 28500 | 70.81%
[29 empty] | 2020 | June | 16 | 9 | 13513 | 28500 | 47.41%
[29 empty] | 2020 | June | 16 | 10 | 22735 | 28500 | 79.77%
[29 empty] | 2020 | June | 16 | 11 | 3650.5 | 28500 | 12.81%
[29 empty] | 2020 | June | 16 | 12 | 26966 | 28500 | 94.62%
[29 empty] | 2020 | June | 16 | 13 | 24448.5 | 28500 | 85.78%
[29 empty] | 2020 | June | 16 | 14 | 16801.5 | 28500 | 58.95%
[29 empty] | 2020 | June | 16 | 15 | 16675.5 | 28500 | 58.51%
[29 empty] | 2020 | June | 16 | 16 | 18819.5 | 28500 | 66.03%
[29 empty] | 2020 | June | 16 | 17 | 9333.5 | 28500 | 32.75%
[29 empty] | 2020 | June | 16 | 18 | 2805 | 28500 | 9.842%
[29 empty] | 2020 | June | 16 | 19 | 1138 | 28500 | 3.993%
[29 empty] | 2020 | June | 16 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 16 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 16 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 16 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 17 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 17 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 17 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 17 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 17 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 17 | 5 | 1963.5 | 28500 | 6.889%
[29 empty] | 2020 | June | 17 | 6 | 3254 | 28500 | 11.42%
[29 empty] | 2020 | June | 17 | 7 | 8698.5 | 28500 | 30.52%
[29 empty] | 2020 | June | 17 | 8 | 13969 | 28500 | 49.01%
[29 empty] | 2020 | June | 17 | 9 | 18633.5 | 28500 | 65.38%
[29 empty] | 2020 | June | 17 | 10 | 19599 | 28500 | 68.77%
[29 empty] | 2020 | June | 17 | 11 | 13503 | 28500 | 47.38%
[29 empty] | 2020 | June | 17 | 12 | 9940.5 | 28500 | 34.88%
[29 empty] | 2020 | June | 17 | 13 | 8121.5 | 28500 | 28.5%
[29 empty] | 2020 | June | 17 | 14 | 6082.5 | 28500 | 21.34%
[29 empty] | 2020 | June | 17 | 15 | 3140 | 28500 | 11.02%
[29 empty] | 2020 | June | 17 | 16 | 5559 | 28500 | 19.51%
[29 empty] | 2020 | June | 17 | 17 | 2310.5 | 28500 | 8.107%
[29 empty] | 2020 | June | 17 | 18 | 1394.5 | 28500 | 4.893%
[29 empty] | 2020 | June | 17 | 19 | 1114.5 | 28500 | 3.911%
[29 empty] | 2020 | June | 17 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 17 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 17 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 17 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 18 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 18 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 18 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 18 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 18 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 18 | 5 | 95.5 | 28500 | 0.3351%
[29 empty] | 2020 | June | 18 | 6 | 846 | 28500 | 2.968%
[29 empty] | 2020 | June | 18 | 7 | 4708 | 28500 | 16.52%
[29 empty] | 2020 | June | 18 | 8 | 15132.5 | 28500 | 53.1%
[29 empty] | 2020 | June | 18 | 9 | 5497 | 28500 | 19.29%
[29 empty] | 2020 | June | 18 | 10 | 2529 | 28500 | 8.874%
[29 empty] | 2020 | June | 18 | 11 | 3519 | 28500 | 12.35%
[29 empty] | 2020 | June | 18 | 12 | 9202.5 | 28500 | 32.29%
[29 empty] | 2020 | June | 18 | 13 | 29160 | 28500 | 102.3%
[29 empty] | 2020 | June | 18 | 14 | 30007 | 28500 | 105.3%
[29 empty] | 2020 | June | 18 | 15 | 25126 | 28500 | 88.16%
[29 empty] | 2020 | June | 18 | 16 | 18064 | 28500 | 63.38%
[29 empty] | 2020 | June | 18 | 17 | 9383 | 28500 | 32.92%
[29 empty] | 2020 | June | 18 | 18 | 2111.5 | 28500 | 7.409%
[29 empty] | 2020 | June | 18 | 19 | 1120 | 28500 | 3.93%
[29 empty] | 2020 | June | 18 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 18 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 18 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 18 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 19 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 19 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 19 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 19 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 19 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 19 | 5 | 116.5 | 28500 | 0.4088%
[29 empty] | 2020 | June | 19 | 6 | 946.5 | 28500 | 3.321%
[29 empty] | 2020 | June | 19 | 7 | 2435 | 28500 | 8.544%
[29 empty] | 2020 | June | 19 | 8 | 6558 | 28500 | 23.01%
[29 empty] | 2020 | June | 19 | 9 | 7899 | 28500 | 27.72%
[29 empty] | 2020 | June | 19 | 10 | 20916 | 28500 | 73.39%
[29 empty] | 2020 | June | 19 | 11 | 16798.5 | 28500 | 58.94%
[29 empty] | 2020 | June | 19 | 12 | 10205.5 | 28500 | 35.81%
[29 empty] | 2020 | June | 19 | 13 | 15385.5 | 28500 | 53.98%
[29 empty] | 2020 | June | 19 | 14 | 12742 | 28500 | 44.71%
[29 empty] | 2020 | June | 19 | 15 | 17963 | 28500 | 63.03%
[29 empty] | 2020 | June | 19 | 16 | 11124 | 28500 | 39.03%
[29 empty] | 2020 | June | 19 | 17 | 4300.5 | 28500 | 15.09%
[29 empty] | 2020 | June | 19 | 18 | 3540 | 28500 | 12.42%
[29 empty] | 2020 | June | 19 | 19 | 73.5 | 28500 | 0.2579%
[29 empty] | 2020 | June | 19 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 19 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 19 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 19 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 20 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 20 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 20 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 20 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 20 | 4 | 118 | 28500 | 0.414%
[29 empty] | 2020 | June | 20 | 5 | 1271 | 28500 | 4.46%
[29 empty] | 2020 | June | 20 | 6 | 3946.5 | 28500 | 13.85%
[29 empty] | 2020 | June | 20 | 7 | 10450.5 | 28500 | 36.67%
[29 empty] | 2020 | June | 20 | 8 | 17510.5 | 28500 | 61.44%
[29 empty] | 2020 | June | 20 | 9 | 20182 | 28500 | 70.81%
[29 empty] | 2020 | June | 20 | 10 | 28781 | 28500 | 101%
[29 empty] | 2020 | June | 20 | 11 | 10368.5 | 28500 | 36.38%
[29 empty] | 2020 | June | 20 | 12 | 25632 | 28500 | 89.94%
[29 empty] | 2020 | June | 20 | 13 | 27285.5 | 28500 | 95.74%
[29 empty] | 2020 | June | 20 | 14 | 32125.5 | 28500 | 112.7%
[29 empty] | 2020 | June | 20 | 15 | 25263 | 28500 | 88.64%
[29 empty] | 2020 | June | 20 | 16 | 19229 | 28500 | 67.47%
[29 empty] | 2020 | June | 20 | 17 | 9710.5 | 28500 | 34.07%
[29 empty] | 2020 | June | 20 | 18 | 1821.5 | 28500 | 6.391%
[29 empty] | 2020 | June | 20 | 19 | 1206 | 28500 | 4.232%
[29 empty] | 2020 | June | 20 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 20 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 20 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 20 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 21 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 21 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 21 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 21 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 21 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 21 | 5 | 1751.5 | 28500 | 6.146%
[29 empty] | 2020 | June | 21 | 6 | 1532 | 28500 | 5.375%
[29 empty] | 2020 | June | 21 | 7 | 3041 | 28500 | 10.67%
[29 empty] | 2020 | June | 21 | 8 | 4954.5 | 28500 | 17.38%
[29 empty] | 2020 | June | 21 | 9 | 14607.5 | 28500 | 51.25%
[29 empty] | 2020 | June | 21 | 10 | 29950 | 28500 | 105.1%
[29 empty] | 2020 | June | 21 | 11 | 25218.5 | 28500 | 88.49%
[29 empty] | 2020 | June | 21 | 12 | 29013.5 | 28500 | 101.8%
[29 empty] | 2020 | June | 21 | 13 | 28351.5 | 28500 | 99.48%
[29 empty] | 2020 | June | 21 | 14 | 16844.5 | 28500 | 59.1%
[29 empty] | 2020 | June | 21 | 15 | 21217 | 28500 | 74.45%
[29 empty] | 2020 | June | 21 | 16 | 14434 | 28500 | 50.65%
[29 empty] | 2020 | June | 21 | 17 | 9679 | 28500 | 33.96%
[29 empty] | 2020 | June | 21 | 18 | 3083.5 | 28500 | 10.82%
[29 empty] | 2020 | June | 21 | 19 | 1049.5 | 28500 | 3.682%
[29 empty] | 2020 | June | 21 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 21 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 21 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 21 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 22 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 22 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 22 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 22 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 22 | 4 | 38.5 | 28500 | 0.1351%
[29 empty] | 2020 | June | 22 | 5 | 1450 | 28500 | 5.088%
[29 empty] | 2020 | June | 22 | 6 | 3840 | 28500 | 13.47%
[29 empty] | 2020 | June | 22 | 7 | 13201 | 28500 | 46.32%
[29 empty] | 2020 | June | 22 | 8 | 22696 | 28500 | 79.64%
[29 empty] | 2020 | June | 22 | 9 | 30182 | 28500 | 105.9%
[29 empty] | 2020 | June | 22 | 10 | 34868 | 28500 | 122.3%
[29 empty] | 2020 | June | 22 | 11 | 39697.5 | 28500 | 139.3%
[29 empty] | 2020 | June | 22 | 12 | 40898 | 28500 | 143.5%
[29 empty] | 2020 | June | 22 | 13 | 37582.5 | 28500 | 131.9%
[29 empty] | 2020 | June | 22 | 14 | 34143 | 28500 | 119.8%
[29 empty] | 2020 | June | 22 | 15 | 27757.5 | 28500 | 97.39%
[29 empty] | 2020 | June | 22 | 16 | 19446.5 | 28500 | 68.23%
[29 empty] | 2020 | June | 22 | 17 | 9761.5 | 28500 | 34.25%
[29 empty] | 2020 | June | 22 | 18 | 2034.5 | 28500 | 7.139%
[29 empty] | 2020 | June | 22 | 19 | 957 | 28500 | 3.358%
[29 empty] | 2020 | June | 22 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 22 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 22 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 22 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 23 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 23 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 23 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 23 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 23 | 4 | 37.5 | 28500 | 0.1316%
[29 empty] | 2020 | June | 23 | 5 | 1631.5 | 28500 | 5.725%
[29 empty] | 2020 | June | 23 | 6 | 3992.5 | 28500 | 14.01%
[29 empty] | 2020 | June | 23 | 7 | 12800.5 | 28500 | 44.91%
[29 empty] | 2020 | June | 23 | 8 | 22057 | 28500 | 77.39%
[29 empty] | 2020 | June | 23 | 9 | 29640 | 28500 | 104%
[29 empty] | 2020 | June | 23 | 10 | 34968.5 | 28500 | 122.7%
[29 empty] | 2020 | June | 23 | 11 | 38194 | 28500 | 134%
[29 empty] | 2020 | June | 23 | 12 | 38523 | 28500 | 135.2%
[29 empty] | 2020 | June | 23 | 13 | 36658 | 28500 | 128.6%
[29 empty] | 2020 | June | 23 | 14 | 32738.5 | 28500 | 114.9%
[29 empty] | 2020 | June | 23 | 15 | 26448.5 | 28500 | 92.8%
[29 empty] | 2020 | June | 23 | 16 | 18512 | 28500 | 64.95%
[29 empty] | 2020 | June | 23 | 17 | 9465 | 28500 | 33.21%
[29 empty] | 2020 | June | 23 | 18 | 3315.5 | 28500 | 11.63%
[29 empty] | 2020 | June | 23 | 19 | 1023 | 28500 | 3.589%
[29 empty] | 2020 | June | 23 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 23 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 23 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 23 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 24 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 24 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 24 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 24 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 24 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 24 | 5 | 1898.5 | 28500 | 6.661%
[29 empty] | 2020 | June | 24 | 6 | 4473 | 28500 | 15.69%
[29 empty] | 2020 | June | 24 | 7 | 12553.5 | 28500 | 44.05%
[29 empty] | 2020 | June | 24 | 8 | 21492 | 28500 | 75.41%
[29 empty] | 2020 | June | 24 | 9 | 29278 | 28500 | 102.7%
[29 empty] | 2020 | June | 24 | 10 | 35038 | 28500 | 122.9%
[29 empty] | 2020 | June | 24 | 11 | 38138.5 | 28500 | 133.8%
[29 empty] | 2020 | June | 24 | 12 | 38608 | 28500 | 135.5%
[29 empty] | 2020 | June | 24 | 13 | 37144.5 | 28500 | 130.3%
[29 empty] | 2020 | June | 24 | 14 | 33313 | 28500 | 116.9%
[29 empty] | 2020 | June | 24 | 15 | 27067 | 28500 | 94.97%
[29 empty] | 2020 | June | 24 | 16 | 18995 | 28500 | 66.65%
[29 empty] | 2020 | June | 24 | 17 | 9565 | 28500 | 33.56%
[29 empty] | 2020 | June | 24 | 18 | 2112.5 | 28500 | 7.412%
[29 empty] | 2020 | June | 24 | 19 | 989.5 | 28500 | 3.472%
[29 empty] | 2020 | June | 24 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 24 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 24 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 24 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 25 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 25 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 25 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 25 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 25 | 4 | 35 | 28500 | 0.1228%
[29 empty] | 2020 | June | 25 | 5 | 1457.5 | 28500 | 5.114%
[29 empty] | 2020 | June | 25 | 6 | 3755.5 | 28500 | 13.18%
[29 empty] | 2020 | June | 25 | 7 | 12779 | 28500 | 44.84%
[29 empty] | 2020 | June | 25 | 8 | 22065.5 | 28500 | 77.42%
[29 empty] | 2020 | June | 25 | 9 | 29528.5 | 28500 | 103.6%
[29 empty] | 2020 | June | 25 | 10 | 34843.5 | 28500 | 122.3%
[29 empty] | 2020 | June | 25 | 11 | 37751 | 28500 | 132.5%
[29 empty] | 2020 | June | 25 | 12 | 38567 | 28500 | 135.3%
[29 empty] | 2020 | June | 25 | 13 | 37022.5 | 28500 | 129.9%
[29 empty] | 2020 | June | 25 | 14 | 32972.5 | 28500 | 115.7%
[29 empty] | 2020 | June | 25 | 15 | 26653.5 | 28500 | 93.52%
[29 empty] | 2020 | June | 25 | 16 | 18862.5 | 28500 | 66.18%
[29 empty] | 2020 | June | 25 | 17 | 9537.5 | 28500 | 33.46%
[29 empty] | 2020 | June | 25 | 18 | 2083.5 | 28500 | 7.311%
[29 empty] | 2020 | June | 25 | 19 | 953.5 | 28500 | 3.346%
[29 empty] | 2020 | June | 25 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 25 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 25 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 25 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 26 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 26 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 26 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 26 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 26 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 26 | 5 | 1746.5 | 28500 | 6.128%
[29 empty] | 2020 | June | 26 | 6 | 4209 | 28500 | 14.77%
[29 empty] | 2020 | June | 26 | 7 | 11358 | 28500 | 39.85%
[29 empty] | 2020 | June | 26 | 8 | 19561.5 | 28500 | 68.64%
[29 empty] | 2020 | June | 26 | 9 | 28418.5 | 28500 | 99.71%
[29 empty] | 2020 | June | 26 | 10 | 34134.5 | 28500 | 119.8%
[29 empty] | 2020 | June | 26 | 11 | 36960 | 28500 | 129.7%
[29 empty] | 2020 | June | 26 | 12 | 37926 | 28500 | 133.1%
[29 empty] | 2020 | June | 26 | 13 | 36461.5 | 28500 | 127.9%
[29 empty] | 2020 | June | 26 | 14 | 32778.5 | 28500 | 115%
[29 empty] | 2020 | June | 26 | 15 | 26830 | 28500 | 94.14%
[29 empty] | 2020 | June | 26 | 16 | 18832 | 28500 | 66.08%
[29 empty] | 2020 | June | 26 | 17 | 9492.5 | 28500 | 33.31%
[29 empty] | 2020 | June | 26 | 18 | 3607.5 | 28500 | 12.66%
[29 empty] | 2020 | June | 26 | 19 | 887 | 28500 | 3.112%
[29 empty] | 2020 | June | 26 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 26 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 26 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 26 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 27 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 27 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 27 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 27 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 27 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 27 | 5 | 1221.5 | 28500 | 4.286%
[29 empty] | 2020 | June | 27 | 6 | 4954.5 | 28500 | 17.38%
[29 empty] | 2020 | June | 27 | 7 | 6320 | 28500 | 22.18%
[29 empty] | 2020 | June | 27 | 8 | 4182.5 | 28500 | 14.68%
[29 empty] | 2020 | June | 27 | 9 | 3747 | 28500 | 13.15%
[29 empty] | 2020 | June | 27 | 10 | 13433 | 28500 | 47.13%
[29 empty] | 2020 | June | 27 | 11 | 4489 | 28500 | 15.75%
[29 empty] | 2020 | June | 27 | 12 | 15123.5 | 28500 | 53.06%
[29 empty] | 2020 | June | 27 | 13 | 11953.5 | 28500 | 41.94%
[29 empty] | 2020 | June | 27 | 14 | 5439 | 28500 | 19.08%
[29 empty] | 2020 | June | 27 | 15 | 12537 | 28500 | 43.99%
[29 empty] | 2020 | June | 27 | 16 | 5296.5 | 28500 | 18.58%
[29 empty] | 2020 | June | 27 | 17 | 8199 | 28500 | 28.77%
[29 empty] | 2020 | June | 27 | 18 | 1544 | 28500 | 5.418%
[29 empty] | 2020 | June | 27 | 19 | 463.5 | 28500 | 1.626%
[29 empty] | 2020 | June | 27 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 27 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 27 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 27 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 28 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 28 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 28 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 28 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 28 | 4 | 37.5 | 28500 | 0.1316%
[29 empty] | 2020 | June | 28 | 5 | 1337 | 28500 | 4.691%
[29 empty] | 2020 | June | 28 | 6 | 3902 | 28500 | 13.69%
[29 empty] | 2020 | June | 28 | 7 | 12980.5 | 28500 | 45.55%
[29 empty] | 2020 | June | 28 | 8 | 21284.5 | 28500 | 74.68%
[29 empty] | 2020 | June | 28 | 9 | 25455.5 | 28500 | 89.32%
[29 empty] | 2020 | June | 28 | 10 | 24098 | 28500 | 84.55%
[29 empty] | 2020 | June | 28 | 11 | 25945.5 | 28500 | 91.04%
[29 empty] | 2020 | June | 28 | 12 | 9395 | 28500 | 32.96%
[29 empty] | 2020 | June | 28 | 13 | 25668 | 28500 | 90.06%
[29 empty] | 2020 | June | 28 | 14 | 29917.5 | 28500 | 105%
[29 empty] | 2020 | June | 28 | 15 | 25572 | 28500 | 89.73%
[29 empty] | 2020 | June | 28 | 16 | 18276.5 | 28500 | 64.13%
[29 empty] | 2020 | June | 28 | 17 | 10236 | 28500 | 35.92%
[29 empty] | 2020 | June | 28 | 18 | 2068.5 | 28500 | 7.258%
[29 empty] | 2020 | June | 28 | 19 | 904 | 28500 | 3.172%
[29 empty] | 2020 | June | 28 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 28 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 28 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 28 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 29 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 29 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 29 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 29 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 29 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 29 | 5 | 1741.5 | 28500 | 6.111%
[29 empty] | 2020 | June | 29 | 6 | 3475.5 | 28500 | 12.19%
[29 empty] | 2020 | June | 29 | 7 | 6271 | 28500 | 22%
[29 empty] | 2020 | June | 29 | 8 | 15207.5 | 28500 | 53.36%
[29 empty] | 2020 | June | 29 | 9 | 13369.5 | 28500 | 46.91%
[29 empty] | 2020 | June | 29 | 10 | 17266 | 28500 | 60.58%
[29 empty] | 2020 | June | 29 | 11 | 36027 | 28500 | 126.4%
[29 empty] | 2020 | June | 29 | 12 | 28904 | 28500 | 101.4%
[29 empty] | 2020 | June | 29 | 13 | 24962.5 | 28500 | 87.59%
[29 empty] | 2020 | June | 29 | 14 | 27502 | 28500 | 96.5%
[29 empty] | 2020 | June | 29 | 15 | 21900.5 | 28500 | 76.84%
[29 empty] | 2020 | June | 29 | 16 | 6523.5 | 28500 | 22.89%
[29 empty] | 2020 | June | 29 | 17 | 5973 | 28500 | 20.96%
[29 empty] | 2020 | June | 29 | 18 | 2161.5 | 28500 | 7.584%
[29 empty] | 2020 | June | 29 | 19 | 905.5 | 28500 | 3.177%
[29 empty] | 2020 | June | 29 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 29 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 29 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 29 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 30 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 30 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 30 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 30 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 30 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 30 | 5 | 1771.5 | 28500 | 6.216%
[29 empty] | 2020 | June | 30 | 6 | 4530.5 | 28500 | 15.9%
[29 empty] | 2020 | June | 30 | 7 | 4349.5 | 28500 | 15.26%
[29 empty] | 2020 | June | 30 | 8 | 3758 | 28500 | 13.19%
[29 empty] | 2020 | June | 30 | 9 | 5516 | 28500 | 19.35%
[29 empty] | 2020 | June | 30 | 10 | 5357 | 28500 | 18.8%
[29 empty] | 2020 | June | 30 | 11 | 5077.5 | 28500 | 17.82%
[29 empty] | 2020 | June | 30 | 12 | 9485 | 28500 | 33.28%
[29 empty] | 2020 | June | 30 | 13 | 5539 | 28500 | 19.44%
[29 empty] | 2020 | June | 30 | 14 | 4691 | 28500 | 16.46%
[29 empty] | 2020 | June | 30 | 15 | 4647.5 | 28500 | 16.31%
[29 empty] | 2020 | June | 30 | 16 | 5416 | 28500 | 19%
[29 empty] | 2020 | June | 30 | 17 | 2163.5 | 28500 | 7.591%
[29 empty] | 2020 | June | 30 | 18 | 936.5 | 28500 | 3.286%
[29 empty] | 2020 | June | 30 | 19 | 73.5 | 28500 | 0.2579%
[29 empty] | 2020 | June | 30 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 30 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 30 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | June | 30 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 1 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 1 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 1 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 1 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 1 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 1 | 5 | 1325.5 | 28500 | 4.651%
[29 empty] | 2020 | July | 1 | 6 | 3738 | 28500 | 13.12%
[29 empty] | 2020 | July | 1 | 7 | 12224.5 | 28500 | 42.89%
[29 empty] | 2020 | July | 1 | 8 | 21726 | 28500 | 76.23%
[29 empty] | 2020 | July | 1 | 9 | 21458 | 28500 | 75.29%
[29 empty] | 2020 | July | 1 | 10 | 14878 | 28500 | 52.2%
[29 empty] | 2020 | July | 1 | 11 | 13529 | 28500 | 47.47%
[29 empty] | 2020 | July | 1 | 12 | 34972.5 | 28500 | 122.7%
[29 empty] | 2020 | July | 1 | 13 | 3699 | 28500 | 12.98%
[29 empty] | 2020 | July | 1 | 14 | 4834 | 28500 | 16.96%
[29 empty] | 2020 | July | 1 | 15 | 3026.5 | 28500 | 10.62%
[29 empty] | 2020 | July | 1 | 16 | 2770.5 | 28500 | 9.721%
[29 empty] | 2020 | July | 1 | 17 | 3245 | 28500 | 11.39%
[29 empty] | 2020 | July | 1 | 18 | 1230 | 28500 | 4.316%
[29 empty] | 2020 | July | 1 | 19 | 574 | 28500 | 2.014%
[29 empty] | 2020 | July | 1 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 1 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 1 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 1 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 2 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 2 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 2 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 2 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 2 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 2 | 5 | 1769 | 28500 | 6.207%
[29 empty] | 2020 | July | 2 | 6 | 3411.5 | 28500 | 11.97%
[29 empty] | 2020 | July | 2 | 7 | 12891 | 28500 | 45.23%
[29 empty] | 2020 | July | 2 | 8 | 6619 | 28500 | 23.22%
[29 empty] | 2020 | July | 2 | 9 | 12928.5 | 28500 | 45.36%
[29 empty] | 2020 | July | 2 | 10 | 5972.5 | 28500 | 20.96%
[29 empty] | 2020 | July | 2 | 11 | 27166 | 28500 | 95.32%
[29 empty] | 2020 | July | 2 | 12 | 14900.5 | 28500 | 52.28%
[29 empty] | 2020 | July | 2 | 13 | 13697.5 | 28500 | 48.06%
[29 empty] | 2020 | July | 2 | 14 | 32147.5 | 28500 | 112.8%
[29 empty] | 2020 | July | 2 | 15 | 12616 | 28500 | 44.27%
[29 empty] | 2020 | July | 2 | 16 | 13921.5 | 28500 | 48.85%
[29 empty] | 2020 | July | 2 | 17 | 9975.5 | 28500 | 35%
[29 empty] | 2020 | July | 2 | 18 | 1028 | 28500 | 3.607%
[29 empty] | 2020 | July | 2 | 19 | 18.5 | 28500 | 0.06491%
[29 empty] | 2020 | July | 2 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 2 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 2 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 2 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 3 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 3 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 3 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 3 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 3 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 3 | 5 | 1571 | 28500 | 5.512%
[29 empty] | 2020 | July | 3 | 6 | 3915 | 28500 | 13.74%
[29 empty] | 2020 | July | 3 | 7 | 12486 | 28500 | 43.81%
[29 empty] | 2020 | July | 3 | 8 | 19135.5 | 28500 | 67.14%
[29 empty] | 2020 | July | 3 | 9 | 18702.5 | 28500 | 65.62%
[29 empty] | 2020 | July | 3 | 10 | 29418 | 28500 | 103.2%
[29 empty] | 2020 | July | 3 | 11 | 36837.5 | 28500 | 129.3%
[29 empty] | 2020 | July | 3 | 12 | 33301 | 28500 | 116.8%
[29 empty] | 2020 | July | 3 | 13 | 30194.5 | 28500 | 105.9%
[29 empty] | 2020 | July | 3 | 14 | 29493.5 | 28500 | 103.5%
[29 empty] | 2020 | July | 3 | 15 | 16359.5 | 28500 | 57.4%
[29 empty] | 2020 | July | 3 | 16 | 11243 | 28500 | 39.45%
[29 empty] | 2020 | July | 3 | 17 | 5575.5 | 28500 | 19.56%
[29 empty] | 2020 | July | 3 | 18 | 550.5 | 28500 | 1.932%
[29 empty] | 2020 | July | 3 | 19 | 94 | 28500 | 0.3298%
[29 empty] | 2020 | July | 3 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 3 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 3 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 3 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 4 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 4 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 4 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 4 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 4 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 4 | 5 | 1513 | 28500 | 5.309%
[29 empty] | 2020 | July | 4 | 6 | 1244.5 | 28500 | 4.367%
[29 empty] | 2020 | July | 4 | 7 | 2023 | 28500 | 7.098%
[29 empty] | 2020 | July | 4 | 8 | 9633.5 | 28500 | 33.8%
[29 empty] | 2020 | July | 4 | 9 | 8597 | 28500 | 30.16%
[29 empty] | 2020 | July | 4 | 10 | 6414.5 | 28500 | 22.51%
[29 empty] | 2020 | July | 4 | 11 | 8227.5 | 28500 | 28.87%
[29 empty] | 2020 | July | 4 | 12 | 7490.5 | 28500 | 26.28%
[29 empty] | 2020 | July | 4 | 13 | 5638.5 | 28500 | 19.78%
[29 empty] | 2020 | July | 4 | 14 | 12457 | 28500 | 43.71%
[29 empty] | 2020 | July | 4 | 15 | 5537 | 28500 | 19.43%
[29 empty] | 2020 | July | 4 | 16 | 4775 | 28500 | 16.75%
[29 empty] | 2020 | July | 4 | 17 | 4554 | 28500 | 15.98%
[29 empty] | 2020 | July | 4 | 18 | 1439.5 | 28500 | 5.051%
[29 empty] | 2020 | July | 4 | 19 | 545 | 28500 | 1.912%
[29 empty] | 2020 | July | 4 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 4 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 4 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 4 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 5 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 5 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 5 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 5 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 5 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 5 | 5 | 902 | 28500 | 3.165%
[29 empty] | 2020 | July | 5 | 6 | 3473.5 | 28500 | 12.19%
[29 empty] | 2020 | July | 5 | 7 | 7807.5 | 28500 | 27.39%
[29 empty] | 2020 | July | 5 | 8 | 18147 | 28500 | 63.67%
[29 empty] | 2020 | July | 5 | 9 | 29235.5 | 28500 | 102.6%
[29 empty] | 2020 | July | 5 | 10 | 34850.5 | 28500 | 122.3%
[29 empty] | 2020 | July | 5 | 11 | 39327.5 | 28500 | 138%
[29 empty] | 2020 | July | 5 | 12 | 40745.5 | 28500 | 143%
[29 empty] | 2020 | July | 5 | 13 | 38950.5 | 28500 | 136.7%
[29 empty] | 2020 | July | 5 | 14 | 32447.5 | 28500 | 113.9%
[29 empty] | 2020 | July | 5 | 15 | 29502.5 | 28500 | 103.5%
[29 empty] | 2020 | July | 5 | 16 | 18851.5 | 28500 | 66.15%
[29 empty] | 2020 | July | 5 | 17 | 10233.5 | 28500 | 35.91%
[29 empty] | 2020 | July | 5 | 18 | 3110.5 | 28500 | 10.91%
[29 empty] | 2020 | July | 5 | 19 | 996.5 | 28500 | 3.496%
[29 empty] | 2020 | July | 5 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 5 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 5 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 5 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 6 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 6 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 6 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 6 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 6 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 6 | 5 | 1409 | 28500 | 4.944%
[29 empty] | 2020 | July | 6 | 6 | 3187 | 28500 | 11.18%
[29 empty] | 2020 | July | 6 | 7 | 12557 | 28500 | 44.06%
[29 empty] | 2020 | July | 6 | 8 | 17831.5 | 28500 | 62.57%
[29 empty] | 2020 | July | 6 | 9 | 7915.5 | 28500 | 27.77%
[29 empty] | 2020 | July | 6 | 10 | 26368 | 28500 | 92.52%
[29 empty] | 2020 | July | 6 | 11 | 21893 | 28500 | 76.82%
[29 empty] | 2020 | July | 6 | 12 | 10905 | 28500 | 38.26%
[29 empty] | 2020 | July | 6 | 13 | 13304 | 28500 | 46.68%
[29 empty] | 2020 | July | 6 | 14 | 23720.5 | 28500 | 83.23%
[29 empty] | 2020 | July | 6 | 15 | 11579.5 | 28500 | 40.63%
[29 empty] | 2020 | July | 6 | 16 | 9933.5 | 28500 | 34.85%
[29 empty] | 2020 | July | 6 | 17 | 8276 | 28500 | 29.04%
[29 empty] | 2020 | July | 6 | 18 | 3601.5 | 28500 | 12.64%
[29 empty] | 2020 | July | 6 | 19 | 1209 | 28500 | 4.242%
[29 empty] | 2020 | July | 6 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 6 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 6 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 6 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 7 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 7 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 7 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 7 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 7 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 7 | 5 | 1405.5 | 28500 | 4.932%
[29 empty] | 2020 | July | 7 | 6 | 3452 | 28500 | 12.11%
[29 empty] | 2020 | July | 7 | 7 | 12381.5 | 28500 | 43.44%
[29 empty] | 2020 | July | 7 | 8 | 21984.5 | 28500 | 77.14%
[29 empty] | 2020 | July | 7 | 9 | 27686.5 | 28500 | 97.15%
[29 empty] | 2020 | July | 7 | 10 | 16590 | 28500 | 58.21%
[29 empty] | 2020 | July | 7 | 11 | 21379.5 | 28500 | 75.02%
[29 empty] | 2020 | July | 7 | 12 | 25099.5 | 28500 | 88.07%
[29 empty] | 2020 | July | 7 | 13 | 17408.5 | 28500 | 61.08%
[29 empty] | 2020 | July | 7 | 14 | 9950.5 | 28500 | 34.91%
[29 empty] | 2020 | July | 7 | 15 | 6993.5 | 28500 | 24.54%
[29 empty] | 2020 | July | 7 | 16 | 5728 | 28500 | 20.1%
[29 empty] | 2020 | July | 7 | 17 | 3789 | 28500 | 13.29%
[29 empty] | 2020 | July | 7 | 18 | 3635 | 28500 | 12.75%
[29 empty] | 2020 | July | 7 | 19 | 330 | 28500 | 1.158%
[29 empty] | 2020 | July | 7 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 7 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 7 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 7 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 8 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 8 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 8 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 8 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 8 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 8 | 5 | 94.5 | 28500 | 0.3316%
[29 empty] | 2020 | July | 8 | 6 | 620 | 28500 | 2.175%
[29 empty] | 2020 | July | 8 | 7 | 3151.5 | 28500 | 11.06%
[29 empty] | 2020 | July | 8 | 8 | 3680.5 | 28500 | 12.91%
[29 empty] | 2020 | July | 8 | 9 | 6137.5 | 28500 | 21.54%
[29 empty] | 2020 | July | 8 | 10 | 6322 | 28500 | 22.18%
[29 empty] | 2020 | July | 8 | 11 | 6346 | 28500 | 22.27%
[29 empty] | 2020 | July | 8 | 12 | 5874.5 | 28500 | 20.61%
[29 empty] | 2020 | July | 8 | 13 | 6061.5 | 28500 | 21.27%
[29 empty] | 2020 | July | 8 | 14 | 8337 | 28500 | 29.25%
[29 empty] | 2020 | July | 8 | 15 | 8838 | 28500 | 31.01%
[29 empty] | 2020 | July | 8 | 16 | 10421.5 | 28500 | 36.57%
[29 empty] | 2020 | July | 8 | 17 | 2137.5 | 28500 | 7.5%
[29 empty] | 2020 | July | 8 | 18 | 2861 | 28500 | 10.04%
[29 empty] | 2020 | July | 8 | 19 | 1082 | 28500 | 3.796%
[29 empty] | 2020 | July | 8 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 8 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 8 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 8 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 9 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 9 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 9 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 9 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 9 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 9 | 5 | 882 | 28500 | 3.095%
[29 empty] | 2020 | July | 9 | 6 | 3636.5 | 28500 | 12.76%
[29 empty] | 2020 | July | 9 | 7 | 5868.5 | 28500 | 20.59%
[29 empty] | 2020 | July | 9 | 8 | 6966.5 | 28500 | 24.44%
[29 empty] | 2020 | July | 9 | 9 | 4844 | 28500 | 17%
[29 empty] | 2020 | July | 9 | 10 | 7634.5 | 28500 | 26.79%
[29 empty] | 2020 | July | 9 | 11 | 5997.5 | 28500 | 21.04%
[29 empty] | 2020 | July | 9 | 12 | 4190.5 | 28500 | 14.7%
[29 empty] | 2020 | July | 9 | 13 | 5447.5 | 28500 | 19.11%
[29 empty] | 2020 | July | 9 | 14 | 3773 | 28500 | 13.24%
[29 empty] | 2020 | July | 9 | 15 | 3880 | 28500 | 13.61%
[29 empty] | 2020 | July | 9 | 16 | 7847.5 | 28500 | 27.54%
[29 empty] | 2020 | July | 9 | 17 | 3891.5 | 28500 | 13.65%
[29 empty] | 2020 | July | 9 | 18 | 767 | 28500 | 2.691%
[29 empty] | 2020 | July | 9 | 19 | 3 | 28500 | 0.01053%
[29 empty] | 2020 | July | 9 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 9 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 9 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 9 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 10 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 10 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 10 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 10 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 10 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 10 | 5 | 338 | 28500 | 1.186%
[29 empty] | 2020 | July | 10 | 6 | 4354.5 | 28500 | 15.28%
[29 empty] | 2020 | July | 10 | 7 | 8376.5 | 28500 | 29.39%
[29 empty] | 2020 | July | 10 | 8 | 9029 | 28500 | 31.68%
[29 empty] | 2020 | July | 10 | 9 | 26724.5 | 28500 | 93.77%
[29 empty] | 2020 | July | 10 | 10 | 33501 | 28500 | 117.5%
[29 empty] | 2020 | July | 10 | 11 | 18670 | 28500 | 65.51%
[29 empty] | 2020 | July | 10 | 12 | 22426 | 28500 | 78.69%
[29 empty] | 2020 | July | 10 | 13 | 14240.5 | 28500 | 49.97%
[29 empty] | 2020 | July | 10 | 14 | 15498 | 28500 | 54.38%
[29 empty] | 2020 | July | 10 | 15 | 17246.5 | 28500 | 60.51%
[29 empty] | 2020 | July | 10 | 16 | 11809.5 | 28500 | 41.44%
[29 empty] | 2020 | July | 10 | 17 | 9386 | 28500 | 32.93%
[29 empty] | 2020 | July | 10 | 18 | 3749 | 28500 | 13.15%
[29 empty] | 2020 | July | 10 | 19 | 842 | 28500 | 2.954%
[29 empty] | 2020 | July | 10 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 10 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 10 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 10 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 11 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 11 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 11 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 11 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 11 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 11 | 5 | 1188.5 | 28500 | 4.17%
[29 empty] | 2020 | July | 11 | 6 | 3210 | 28500 | 11.26%
[29 empty] | 2020 | July | 11 | 7 | 12800 | 28500 | 44.91%
[29 empty] | 2020 | July | 11 | 8 | 21799.5 | 28500 | 76.49%
[29 empty] | 2020 | July | 11 | 9 | 23450.5 | 28500 | 82.28%
[29 empty] | 2020 | July | 11 | 10 | 26548.5 | 28500 | 93.15%
[29 empty] | 2020 | July | 11 | 11 | 31317.5 | 28500 | 109.9%
[29 empty] | 2020 | July | 11 | 12 | 27525.5 | 28500 | 96.58%
[29 empty] | 2020 | July | 11 | 13 | 20001.5 | 28500 | 70.18%
[29 empty] | 2020 | July | 11 | 14 | 22846 | 28500 | 80.16%
[29 empty] | 2020 | July | 11 | 15 | 8015.5 | 28500 | 28.12%
[29 empty] | 2020 | July | 11 | 16 | 16464 | 28500 | 57.77%
[29 empty] | 2020 | July | 11 | 17 | 10004 | 28500 | 35.1%
[29 empty] | 2020 | July | 11 | 18 | 3628.5 | 28500 | 12.73%
[29 empty] | 2020 | July | 11 | 19 | 1022.5 | 28500 | 3.588%
[29 empty] | 2020 | July | 11 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 11 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 11 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 11 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 12 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 12 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 12 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 12 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 12 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 12 | 5 | 1276 | 28500 | 4.477%
[29 empty] | 2020 | July | 12 | 6 | 3248 | 28500 | 11.4%
[29 empty] | 2020 | July | 12 | 7 | 12249 | 28500 | 42.98%
[29 empty] | 2020 | July | 12 | 8 | 20662 | 28500 | 72.5%
[29 empty] | 2020 | July | 12 | 9 | 23124.5 | 28500 | 81.14%
[29 empty] | 2020 | July | 12 | 10 | 26246 | 28500 | 92.09%
[29 empty] | 2020 | July | 12 | 11 | 28050.5 | 28500 | 98.42%
[29 empty] | 2020 | July | 12 | 12 | 32153 | 28500 | 112.8%
[29 empty] | 2020 | July | 12 | 13 | 29768.5 | 28500 | 104.5%
[29 empty] | 2020 | July | 12 | 14 | 28846.5 | 28500 | 101.2%
[29 empty] | 2020 | July | 12 | 15 | 25194 | 28500 | 88.4%
[29 empty] | 2020 | July | 12 | 16 | 17293.5 | 28500 | 60.68%
[29 empty] | 2020 | July | 12 | 17 | 9538 | 28500 | 33.47%
[29 empty] | 2020 | July | 12 | 18 | 2523.5 | 28500 | 8.854%
[29 empty] | 2020 | July | 12 | 19 | 1069.5 | 28500 | 3.753%
[29 empty] | 2020 | July | 12 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 12 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 12 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 12 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 13 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 13 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 13 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 13 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 13 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 13 | 5 | 1440.5 | 28500 | 5.054%
[29 empty] | 2020 | July | 13 | 6 | 3881 | 28500 | 13.62%
[29 empty] | 2020 | July | 13 | 7 | 11240 | 28500 | 39.44%
[29 empty] | 2020 | July | 13 | 8 | 21510 | 28500 | 75.47%
[29 empty] | 2020 | July | 13 | 9 | 29470 | 28500 | 103.4%
[29 empty] | 2020 | July | 13 | 10 | 35326.5 | 28500 | 124%
[29 empty] | 2020 | July | 13 | 11 | 38530.5 | 28500 | 135.2%
[29 empty] | 2020 | July | 13 | 12 | 36026 | 28500 | 126.4%
[29 empty] | 2020 | July | 13 | 13 | 36797.5 | 28500 | 129.1%
[29 empty] | 2020 | July | 13 | 14 | 22527.5 | 28500 | 79.04%
[29 empty] | 2020 | July | 13 | 15 | 22541.5 | 28500 | 79.09%
[29 empty] | 2020 | July | 13 | 16 | 19162.5 | 28500 | 67.24%
[29 empty] | 2020 | July | 13 | 17 | 9636.5 | 28500 | 33.81%
[29 empty] | 2020 | July | 13 | 18 | 3203.5 | 28500 | 11.24%
[29 empty] | 2020 | July | 13 | 19 | 2.5 | 28500 | 0.008772%
[29 empty] | 2020 | July | 13 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 13 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 13 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 13 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 14 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 14 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 14 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 14 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 14 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 14 | 5 | 281 | 28500 | 0.986%
[29 empty] | 2020 | July | 14 | 6 | 3777 | 28500 | 13.25%
[29 empty] | 2020 | July | 14 | 7 | 9182 | 28500 | 32.22%
[29 empty] | 2020 | July | 14 | 8 | 16270.5 | 28500 | 57.09%
[29 empty] | 2020 | July | 14 | 9 | 25109 | 28500 | 88.1%
[29 empty] | 2020 | July | 14 | 10 | 13175 | 28500 | 46.23%
[29 empty] | 2020 | July | 14 | 11 | 10785.5 | 28500 | 37.84%
[29 empty] | 2020 | July | 14 | 12 | 16210.5 | 28500 | 56.88%
[29 empty] | 2020 | July | 14 | 13 | 17313 | 28500 | 60.75%
[29 empty] | 2020 | July | 14 | 14 | 11637 | 28500 | 40.83%
[29 empty] | 2020 | July | 14 | 15 | 6245 | 28500 | 21.91%
[29 empty] | 2020 | July | 14 | 16 | 9461 | 28500 | 33.2%
[29 empty] | 2020 | July | 14 | 17 | 6813.5 | 28500 | 23.91%
[29 empty] | 2020 | July | 14 | 18 | 896.5 | 28500 | 3.146%
[29 empty] | 2020 | July | 14 | 19 | 3 | 28500 | 0.01053%
[29 empty] | 2020 | July | 14 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 14 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 14 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 14 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 15 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 15 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 15 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 15 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 15 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 15 | 5 | 1266.5 | 28500 | 4.444%
[29 empty] | 2020 | July | 15 | 6 | 4090 | 28500 | 14.35%
[29 empty] | 2020 | July | 15 | 7 | 10868 | 28500 | 38.13%
[29 empty] | 2020 | July | 15 | 8 | 19599 | 28500 | 68.77%
[29 empty] | 2020 | July | 15 | 9 | 18183 | 28500 | 63.8%
[29 empty] | 2020 | July | 15 | 10 | 15328.5 | 28500 | 53.78%
[29 empty] | 2020 | July | 15 | 11 | 16753 | 28500 | 58.78%
[29 empty] | 2020 | July | 15 | 12 | 6949 | 28500 | 24.38%
[29 empty] | 2020 | July | 15 | 13 | 11555 | 28500 | 40.54%
[29 empty] | 2020 | July | 15 | 14 | 5903 | 28500 | 20.71%
[29 empty] | 2020 | July | 15 | 15 | 4098 | 28500 | 14.38%
[29 empty] | 2020 | July | 15 | 16 | 3004.5 | 28500 | 10.54%
[29 empty] | 2020 | July | 15 | 17 | 1797.5 | 28500 | 6.307%
[29 empty] | 2020 | July | 15 | 18 | 1376 | 28500 | 4.828%
[29 empty] | 2020 | July | 15 | 19 | 54 | 28500 | 0.1895%
[29 empty] | 2020 | July | 15 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 15 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 15 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 15 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 16 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 16 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 16 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 16 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 16 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 16 | 5 | 386.5 | 28500 | 1.356%
[29 empty] | 2020 | July | 16 | 6 | 1213.5 | 28500 | 4.258%
[29 empty] | 2020 | July | 16 | 7 | 3441.5 | 28500 | 12.08%
[29 empty] | 2020 | July | 16 | 8 | 5266.5 | 28500 | 18.48%
[29 empty] | 2020 | July | 16 | 9 | 4525 | 28500 | 15.88%
[29 empty] | 2020 | July | 16 | 10 | 4745.5 | 28500 | 16.65%
[29 empty] | 2020 | July | 16 | 11 | 5074.5 | 28500 | 17.81%
[29 empty] | 2020 | July | 16 | 12 | 14882.5 | 28500 | 52.22%
[29 empty] | 2020 | July | 16 | 13 | 17176 | 28500 | 60.27%
[29 empty] | 2020 | July | 16 | 14 | 21718 | 28500 | 76.2%
[29 empty] | 2020 | July | 16 | 15 | 13168 | 28500 | 46.2%
[29 empty] | 2020 | July | 16 | 16 | 16603.5 | 28500 | 58.26%
[29 empty] | 2020 | July | 16 | 17 | 8038 | 28500 | 28.2%
[29 empty] | 2020 | July | 16 | 18 | 3326.5 | 28500 | 11.67%
[29 empty] | 2020 | July | 16 | 19 | 374 | 28500 | 1.312%
[29 empty] | 2020 | July | 16 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 16 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 16 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 16 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 17 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 17 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 17 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 17 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 17 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 17 | 5 | 1279 | 28500 | 4.488%
[29 empty] | 2020 | July | 17 | 6 | 3539 | 28500 | 12.42%
[29 empty] | 2020 | July | 17 | 7 | 9427 | 28500 | 33.08%
[29 empty] | 2020 | July | 17 | 8 | 13966.5 | 28500 | 49.01%
[29 empty] | 2020 | July | 17 | 9 | 18933 | 28500 | 66.43%
[29 empty] | 2020 | July | 17 | 10 | 30955.5 | 28500 | 108.6%
[29 empty] | 2020 | July | 17 | 11 | 33456.5 | 28500 | 117.4%
[29 empty] | 2020 | July | 17 | 12 | 32285 | 28500 | 113.3%
[29 empty] | 2020 | July | 17 | 13 | 35305.5 | 28500 | 123.9%
[29 empty] | 2020 | July | 17 | 14 | 29391 | 28500 | 103.1%
[29 empty] | 2020 | July | 17 | 15 | 26832.5 | 28500 | 94.15%
[29 empty] | 2020 | July | 17 | 16 | 18899.5 | 28500 | 66.31%
[29 empty] | 2020 | July | 17 | 17 | 9825 | 28500 | 34.47%
[29 empty] | 2020 | July | 17 | 18 | 2791.5 | 28500 | 9.795%
[29 empty] | 2020 | July | 17 | 19 | 871.5 | 28500 | 3.058%
[29 empty] | 2020 | July | 17 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 17 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 17 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 17 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 18 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 18 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 18 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 18 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 18 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 18 | 5 | 1168 | 28500 | 4.098%
[29 empty] | 2020 | July | 18 | 6 | 3285.5 | 28500 | 11.53%
[29 empty] | 2020 | July | 18 | 7 | 10260.5 | 28500 | 36%
[29 empty] | 2020 | July | 18 | 8 | 18522 | 28500 | 64.99%
[29 empty] | 2020 | July | 18 | 9 | 20775.5 | 28500 | 72.9%
[29 empty] | 2020 | July | 18 | 10 | 25704 | 28500 | 90.19%
[29 empty] | 2020 | July | 18 | 11 | 37313.5 | 28500 | 130.9%
[29 empty] | 2020 | July | 18 | 12 | 38124.5 | 28500 | 133.8%
[29 empty] | 2020 | July | 18 | 13 | 35773.5 | 28500 | 125.5%
[29 empty] | 2020 | July | 18 | 14 | 33918 | 28500 | 119%
[29 empty] | 2020 | July | 18 | 15 | 27836 | 28500 | 97.67%
[29 empty] | 2020 | July | 18 | 16 | 19345.5 | 28500 | 67.88%
[29 empty] | 2020 | July | 18 | 17 | 9906 | 28500 | 34.76%
[29 empty] | 2020 | July | 18 | 18 | 2683 | 28500 | 9.414%
[29 empty] | 2020 | July | 18 | 19 | 730.5 | 28500 | 2.563%
[29 empty] | 2020 | July | 18 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 18 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 18 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 18 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 19 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 19 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 19 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 19 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 19 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 19 | 5 | 1094.5 | 28500 | 3.84%
[29 empty] | 2020 | July | 19 | 6 | 3614 | 28500 | 12.68%
[29 empty] | 2020 | July | 19 | 7 | 7081 | 28500 | 24.85%
[29 empty] | 2020 | July | 19 | 8 | 5650.5 | 28500 | 19.83%
[29 empty] | 2020 | July | 19 | 9 | 6428 | 28500 | 22.55%
[29 empty] | 2020 | July | 19 | 10 | 4546 | 28500 | 15.95%
[29 empty] | 2020 | July | 19 | 11 | 9653 | 28500 | 33.87%
[29 empty] | 2020 | July | 19 | 12 | 11596 | 28500 | 40.69%
[29 empty] | 2020 | July | 19 | 13 | 8671 | 28500 | 30.42%
[29 empty] | 2020 | July | 19 | 14 | 12065.5 | 28500 | 42.34%
[29 empty] | 2020 | July | 19 | 15 | 20607 | 28500 | 72.31%
[29 empty] | 2020 | July | 19 | 16 | 2918 | 28500 | 10.24%
[29 empty] | 2020 | July | 19 | 17 | 3586.5 | 28500 | 12.58%
[29 empty] | 2020 | July | 19 | 18 | 2505.5 | 28500 | 8.791%
[29 empty] | 2020 | July | 19 | 19 | 837 | 28500 | 2.937%
[29 empty] | 2020 | July | 19 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 19 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 19 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 19 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 20 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 20 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 20 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 20 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 20 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 20 | 5 | 1086 | 28500 | 3.811%
[29 empty] | 2020 | July | 20 | 6 | 3026 | 28500 | 10.62%
[29 empty] | 2020 | July | 20 | 7 | 11554 | 28500 | 40.54%
[29 empty] | 2020 | July | 20 | 8 | 20738.5 | 28500 | 72.77%
[29 empty] | 2020 | July | 20 | 9 | 25097 | 28500 | 88.06%
[29 empty] | 2020 | July | 20 | 10 | 32152.5 | 28500 | 112.8%
[29 empty] | 2020 | July | 20 | 11 | 30599.5 | 28500 | 107.4%
[29 empty] | 2020 | July | 20 | 12 | 33139 | 28500 | 116.3%
[29 empty] | 2020 | July | 20 | 13 | 37996 | 28500 | 133.3%
[29 empty] | 2020 | July | 20 | 14 | 32463.5 | 28500 | 113.9%
[29 empty] | 2020 | July | 20 | 15 | 28075.5 | 28500 | 98.51%
[29 empty] | 2020 | July | 20 | 16 | 19759.5 | 28500 | 69.33%
[29 empty] | 2020 | July | 20 | 17 | 10170 | 28500 | 35.68%
[29 empty] | 2020 | July | 20 | 18 | 2686.5 | 28500 | 9.426%
[29 empty] | 2020 | July | 20 | 19 | 862.5 | 28500 | 3.026%
[29 empty] | 2020 | July | 20 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 20 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 20 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 20 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 21 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 21 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 21 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 21 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 21 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 21 | 5 | 1028 | 28500 | 3.607%
[29 empty] | 2020 | July | 21 | 6 | 2971 | 28500 | 10.42%
[29 empty] | 2020 | July | 21 | 7 | 12098.5 | 28500 | 42.45%
[29 empty] | 2020 | July | 21 | 8 | 21952.5 | 28500 | 77.03%
[29 empty] | 2020 | July | 21 | 9 | 29653.5 | 28500 | 104%
[29 empty] | 2020 | July | 21 | 10 | 28495 | 28500 | 99.98%
[29 empty] | 2020 | July | 21 | 11 | 31264 | 28500 | 109.7%
[29 empty] | 2020 | July | 21 | 12 | 32986.5 | 28500 | 115.7%
[29 empty] | 2020 | July | 21 | 13 | 31905 | 28500 | 111.9%
[29 empty] | 2020 | July | 21 | 14 | 30430 | 28500 | 106.8%
[29 empty] | 2020 | July | 21 | 15 | 21781.5 | 28500 | 76.43%
[29 empty] | 2020 | July | 21 | 16 | 18093.5 | 28500 | 63.49%
[29 empty] | 2020 | July | 21 | 17 | 9230 | 28500 | 32.39%
[29 empty] | 2020 | July | 21 | 18 | 3057.5 | 28500 | 10.73%
[29 empty] | 2020 | July | 21 | 19 | 803 | 28500 | 2.818%
[29 empty] | 2020 | July | 21 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 21 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 21 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 21 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 22 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 22 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 22 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 22 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 22 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 22 | 5 | 953 | 28500 | 3.344%
[29 empty] | 2020 | July | 22 | 6 | 2805 | 28500 | 9.842%
[29 empty] | 2020 | July | 22 | 7 | 10396.5 | 28500 | 36.48%
[29 empty] | 2020 | July | 22 | 8 | 18206.5 | 28500 | 63.88%
[29 empty] | 2020 | July | 22 | 9 | 29503 | 28500 | 103.5%
[29 empty] | 2020 | July | 22 | 10 | 34319 | 28500 | 120.4%
[29 empty] | 2020 | July | 22 | 11 | 30442 | 28500 | 106.8%
[29 empty] | 2020 | July | 22 | 12 | 19912 | 28500 | 69.87%
[29 empty] | 2020 | July | 22 | 13 | 27010.5 | 28500 | 94.77%
[29 empty] | 2020 | July | 22 | 14 | 21293 | 28500 | 74.71%
[29 empty] | 2020 | July | 22 | 15 | 25774 | 28500 | 90.44%
[29 empty] | 2020 | July | 22 | 16 | 18369 | 28500 | 64.45%
[29 empty] | 2020 | July | 22 | 17 | 9830 | 28500 | 34.49%
[29 empty] | 2020 | July | 22 | 18 | 2085 | 28500 | 7.316%
[29 empty] | 2020 | July | 22 | 19 | 739 | 28500 | 2.593%
[29 empty] | 2020 | July | 22 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 22 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 22 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 22 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 23 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 23 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 23 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 23 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 23 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 23 | 5 | 558.5 | 28500 | 1.96%
[29 empty] | 2020 | July | 23 | 6 | 3284.5 | 28500 | 11.52%
[29 empty] | 2020 | July | 23 | 7 | 7488.5 | 28500 | 26.28%
[29 empty] | 2020 | July | 23 | 8 | 9217 | 28500 | 32.34%
[29 empty] | 2020 | July | 23 | 9 | 15880 | 28500 | 55.72%
[29 empty] | 2020 | July | 23 | 10 | 21956 | 28500 | 77.04%
[29 empty] | 2020 | July | 23 | 11 | 37016.5 | 28500 | 129.9%
[29 empty] | 2020 | July | 23 | 12 | 13240.5 | 28500 | 46.46%
[29 empty] | 2020 | July | 23 | 13 | 35817.5 | 28500 | 125.7%
[29 empty] | 2020 | July | 23 | 14 | 33033.5 | 28500 | 115.9%
[29 empty] | 2020 | July | 23 | 15 | 27063 | 28500 | 94.96%
[29 empty] | 2020 | July | 23 | 16 | 13703.5 | 28500 | 48.08%
[29 empty] | 2020 | July | 23 | 17 | 7472.5 | 28500 | 26.22%
[29 empty] | 2020 | July | 23 | 18 | 2602.5 | 28500 | 9.132%
[29 empty] | 2020 | July | 23 | 19 | 323.5 | 28500 | 1.135%
[29 empty] | 2020 | July | 23 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 23 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 23 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 23 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 24 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 24 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 24 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 24 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 24 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 24 | 5 | 439 | 28500 | 1.54%
[29 empty] | 2020 | July | 24 | 6 | 3069.5 | 28500 | 10.77%
[29 empty] | 2020 | July | 24 | 7 | 6104.5 | 28500 | 21.42%
[29 empty] | 2020 | July | 24 | 8 | 9107 | 28500 | 31.95%
[29 empty] | 2020 | July | 24 | 9 | 20596.5 | 28500 | 72.27%
[29 empty] | 2020 | July | 24 | 10 | 12865.5 | 28500 | 45.14%
[29 empty] | 2020 | July | 24 | 11 | 13816.5 | 28500 | 48.48%
[29 empty] | 2020 | July | 24 | 12 | 24889.5 | 28500 | 87.33%
[29 empty] | 2020 | July | 24 | 13 | 9018.5 | 28500 | 31.64%
[29 empty] | 2020 | July | 24 | 14 | 11177 | 28500 | 39.22%
[29 empty] | 2020 | July | 24 | 15 | 10228.5 | 28500 | 35.89%
[29 empty] | 2020 | July | 24 | 16 | 13965 | 28500 | 49%
[29 empty] | 2020 | July | 24 | 17 | 9171.5 | 28500 | 32.18%
[29 empty] | 2020 | July | 24 | 18 | 2114.5 | 28500 | 7.419%
[29 empty] | 2020 | July | 24 | 19 | 509 | 28500 | 1.786%
[29 empty] | 2020 | July | 24 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 24 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 24 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 24 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 25 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 25 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 25 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 25 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 25 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 25 | 5 | 329 | 28500 | 1.154%
[29 empty] | 2020 | July | 25 | 6 | 770 | 28500 | 2.702%
[29 empty] | 2020 | July | 25 | 7 | 3761 | 28500 | 13.2%
[29 empty] | 2020 | July | 25 | 8 | 3381 | 28500 | 11.86%
[29 empty] | 2020 | July | 25 | 9 | 4285.5 | 28500 | 15.04%
[29 empty] | 2020 | July | 25 | 10 | 7766.5 | 28500 | 27.25%
[29 empty] | 2020 | July | 25 | 11 | 7635 | 28500 | 26.79%
[29 empty] | 2020 | July | 25 | 12 | 10861 | 28500 | 38.11%
[29 empty] | 2020 | July | 25 | 13 | 7167 | 28500 | 25.15%
[29 empty] | 2020 | July | 25 | 14 | 3675.5 | 28500 | 12.9%
[29 empty] | 2020 | July | 25 | 15 | 2537 | 28500 | 8.902%
[29 empty] | 2020 | July | 25 | 16 | 1864 | 28500 | 6.54%
[29 empty] | 2020 | July | 25 | 17 | 645 | 28500 | 2.263%
[29 empty] | 2020 | July | 25 | 18 | 237 | 28500 | 0.8316%
[29 empty] | 2020 | July | 25 | 19 | 692 | 28500 | 2.428%
[29 empty] | 2020 | July | 25 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 25 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 25 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 25 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 26 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 26 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 26 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 26 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 26 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 26 | 5 | 828.5 | 28500 | 2.907%
[29 empty] | 2020 | July | 26 | 6 | 2644.5 | 28500 | 9.279%
[29 empty] | 2020 | July | 26 | 7 | 6664 | 28500 | 23.38%
[29 empty] | 2020 | July | 26 | 8 | 10798 | 28500 | 37.89%
[29 empty] | 2020 | July | 26 | 9 | 23061 | 28500 | 80.92%
[29 empty] | 2020 | July | 26 | 10 | 14379.5 | 28500 | 50.45%
[29 empty] | 2020 | July | 26 | 11 | 23175 | 28500 | 81.32%
[29 empty] | 2020 | July | 26 | 12 | 29313 | 28500 | 102.9%
[29 empty] | 2020 | July | 26 | 13 | 28459.5 | 28500 | 99.86%
[29 empty] | 2020 | July | 26 | 14 | 16229 | 28500 | 56.94%
[29 empty] | 2020 | July | 26 | 15 | 6538 | 28500 | 22.94%
[29 empty] | 2020 | July | 26 | 16 | 5788.5 | 28500 | 20.31%
[29 empty] | 2020 | July | 26 | 17 | 5961 | 28500 | 20.92%
[29 empty] | 2020 | July | 26 | 18 | 2987 | 28500 | 10.48%
[29 empty] | 2020 | July | 26 | 19 | 113 | 28500 | 0.3965%
[29 empty] | 2020 | July | 26 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 26 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 26 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 26 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 27 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 27 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 27 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 27 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 27 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 27 | 5 | 36.5 | 28500 | 0.1281%
[29 empty] | 2020 | July | 27 | 6 | 649.5 | 28500 | 2.279%
[29 empty] | 2020 | July | 27 | 7 | 2538 | 28500 | 8.905%
[29 empty] | 2020 | July | 27 | 8 | 4411 | 28500 | 15.48%
[29 empty] | 2020 | July | 27 | 9 | 5205.5 | 28500 | 18.26%
[29 empty] | 2020 | July | 27 | 10 | 28126.5 | 28500 | 98.69%
[29 empty] | 2020 | July | 27 | 11 | 3102 | 28500 | 10.88%
[29 empty] | 2020 | July | 27 | 12 | 4175 | 28500 | 14.65%
[29 empty] | 2020 | July | 27 | 13 | 11096 | 28500 | 38.93%
[29 empty] | 2020 | July | 27 | 14 | 4940 | 28500 | 17.33%
[29 empty] | 2020 | July | 27 | 15 | 6744 | 28500 | 23.66%
[29 empty] | 2020 | July | 27 | 16 | 8572.5 | 28500 | 30.08%
[29 empty] | 2020 | July | 27 | 17 | 5624 | 28500 | 19.73%
[29 empty] | 2020 | July | 27 | 18 | 2067.5 | 28500 | 7.254%
[29 empty] | 2020 | July | 27 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 27 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 27 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 27 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 27 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 28 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 28 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 28 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 28 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 28 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 28 | 5 | 797.5 | 28500 | 2.798%
[29 empty] | 2020 | July | 28 | 6 | 2773.5 | 28500 | 9.732%
[29 empty] | 2020 | July | 28 | 7 | 10601 | 28500 | 37.2%
[29 empty] | 2020 | July | 28 | 8 | 21820.5 | 28500 | 76.56%
[29 empty] | 2020 | July | 28 | 9 | 21334.5 | 28500 | 74.86%
[29 empty] | 2020 | July | 28 | 10 | 27848.5 | 28500 | 97.71%
[29 empty] | 2020 | July | 28 | 11 | 19555.5 | 28500 | 68.62%
[29 empty] | 2020 | July | 28 | 12 | 23558 | 28500 | 82.66%
[29 empty] | 2020 | July | 28 | 13 | 22201 | 28500 | 77.9%
[29 empty] | 2020 | July | 28 | 14 | 21772.5 | 28500 | 76.39%
[29 empty] | 2020 | July | 28 | 15 | 11839.5 | 28500 | 41.54%
[29 empty] | 2020 | July | 28 | 16 | 14270.5 | 28500 | 50.07%
[29 empty] | 2020 | July | 28 | 17 | 9132 | 28500 | 32.04%
[29 empty] | 2020 | July | 28 | 18 | 3004 | 28500 | 10.54%
[29 empty] | 2020 | July | 28 | 19 | 407 | 28500 | 1.428%
[29 empty] | 2020 | July | 28 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 28 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 28 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 28 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 29 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 29 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 29 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 29 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 29 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 29 | 5 | 775.5 | 28500 | 2.721%
[29 empty] | 2020 | July | 29 | 6 | 2825 | 28500 | 9.912%
[29 empty] | 2020 | July | 29 | 7 | 11369 | 28500 | 39.89%
[29 empty] | 2020 | July | 29 | 8 | 21406 | 28500 | 75.11%
[29 empty] | 2020 | July | 29 | 9 | 28068 | 28500 | 98.48%
[29 empty] | 2020 | July | 29 | 10 | 34847.5 | 28500 | 122.3%
[29 empty] | 2020 | July | 29 | 11 | 38083 | 28500 | 133.6%
[29 empty] | 2020 | July | 29 | 12 | 39873 | 28500 | 139.9%
[29 empty] | 2020 | July | 29 | 13 | 39294.5 | 28500 | 137.9%
[29 empty] | 2020 | July | 29 | 14 | 30719 | 28500 | 107.8%
[29 empty] | 2020 | July | 29 | 15 | 22952 | 28500 | 80.53%
[29 empty] | 2020 | July | 29 | 16 | 18941 | 28500 | 66.46%
[29 empty] | 2020 | July | 29 | 17 | 8379.5 | 28500 | 29.4%
[29 empty] | 2020 | July | 29 | 18 | 2801.5 | 28500 | 9.83%
[29 empty] | 2020 | July | 29 | 19 | 456.5 | 28500 | 1.602%
[29 empty] | 2020 | July | 29 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 29 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 29 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 29 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 30 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 30 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 30 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 30 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 30 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 30 | 5 | 679.5 | 28500 | 2.384%
[29 empty] | 2020 | July | 30 | 6 | 2613 | 28500 | 9.168%
[29 empty] | 2020 | July | 30 | 7 | 11330.5 | 28500 | 39.76%
[29 empty] | 2020 | July | 30 | 8 | 21223 | 28500 | 74.47%
[29 empty] | 2020 | July | 30 | 9 | 28927 | 28500 | 101.5%
[29 empty] | 2020 | July | 30 | 10 | 34909 | 28500 | 122.5%
[29 empty] | 2020 | July | 30 | 11 | 38838.5 | 28500 | 136.3%
[29 empty] | 2020 | July | 30 | 12 | 38228.5 | 28500 | 134.1%
[29 empty] | 2020 | July | 30 | 13 | 37617.5 | 28500 | 132%
[29 empty] | 2020 | July | 30 | 14 | 34053.5 | 28500 | 119.5%
[29 empty] | 2020 | July | 30 | 15 | 24616 | 28500 | 86.37%
[29 empty] | 2020 | July | 30 | 16 | 19428.5 | 28500 | 68.17%
[29 empty] | 2020 | July | 30 | 17 | 9300 | 28500 | 32.63%
[29 empty] | 2020 | July | 30 | 18 | 1398 | 28500 | 4.905%
[29 empty] | 2020 | July | 30 | 19 | 447 | 28500 | 1.568%
[29 empty] | 2020 | July | 30 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 30 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 30 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 30 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 31 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 31 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 31 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 31 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 31 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 31 | 5 | 719 | 28500 | 2.523%
[29 empty] | 2020 | July | 31 | 6 | 2677 | 28500 | 9.393%
[29 empty] | 2020 | July | 31 | 7 | 10916 | 28500 | 38.3%
[29 empty] | 2020 | July | 31 | 8 | 20449 | 28500 | 71.75%
[29 empty] | 2020 | July | 31 | 9 | 28011.5 | 28500 | 98.29%
[29 empty] | 2020 | July | 31 | 10 | 33312.5 | 28500 | 116.9%
[29 empty] | 2020 | July | 31 | 11 | 37981.5 | 28500 | 133.3%
[29 empty] | 2020 | July | 31 | 12 | 38714 | 28500 | 135.8%
[29 empty] | 2020 | July | 31 | 13 | 37244.5 | 28500 | 130.7%
[29 empty] | 2020 | July | 31 | 14 | 33024.5 | 28500 | 115.9%
[29 empty] | 2020 | July | 31 | 15 | 22001 | 28500 | 77.2%
[29 empty] | 2020 | July | 31 | 16 | 10048 | 28500 | 35.26%
[29 empty] | 2020 | July | 31 | 17 | 1237.5 | 28500 | 4.342%
[29 empty] | 2020 | July | 31 | 18 | 1996 | 28500 | 7.004%
[29 empty] | 2020 | July | 31 | 19 | 266.5 | 28500 | 0.9351%
[29 empty] | 2020 | July | 31 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 31 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 31 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | July | 31 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 1 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 1 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 1 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 1 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 1 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 1 | 5 | 658.5 | 28500 | 2.311%
[29 empty] | 2020 | August | 1 | 6 | 2557.5 | 28500 | 8.974%
[29 empty] | 2020 | August | 1 | 7 | 11340 | 28500 | 39.79%
[29 empty] | 2020 | August | 1 | 8 | 21140 | 28500 | 74.18%
[29 empty] | 2020 | August | 1 | 9 | 27364 | 28500 | 96.01%
[29 empty] | 2020 | August | 1 | 10 | 15196 | 28500 | 53.32%
[29 empty] | 2020 | August | 1 | 11 | 21101 | 28500 | 74.04%
[29 empty] | 2020 | August | 1 | 12 | 13375 | 28500 | 46.93%
[29 empty] | 2020 | August | 1 | 13 | 14591 | 28500 | 51.2%
[29 empty] | 2020 | August | 1 | 14 | 13334 | 28500 | 46.79%
[29 empty] | 2020 | August | 1 | 15 | 19133 | 28500 | 67.13%
[29 empty] | 2020 | August | 1 | 16 | 8735.5 | 28500 | 30.65%
[29 empty] | 2020 | August | 1 | 17 | 8798.5 | 28500 | 30.87%
[29 empty] | 2020 | August | 1 | 18 | 2627 | 28500 | 9.218%
[29 empty] | 2020 | August | 1 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 1 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 1 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 1 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 1 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 2 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 2 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 2 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 2 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 2 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 2 | 5 | 584 | 28500 | 2.049%
[29 empty] | 2020 | August | 2 | 6 | 2480 | 28500 | 8.702%
[29 empty] | 2020 | August | 2 | 7 | 11613.5 | 28500 | 40.75%
[29 empty] | 2020 | August | 2 | 8 | 21695.5 | 28500 | 76.12%
[29 empty] | 2020 | August | 2 | 9 | 18953.5 | 28500 | 66.5%
[29 empty] | 2020 | August | 2 | 10 | 26621.5 | 28500 | 93.41%
[29 empty] | 2020 | August | 2 | 11 | 33678.5 | 28500 | 118.2%
[29 empty] | 2020 | August | 2 | 12 | 38791 | 28500 | 136.1%
[29 empty] | 2020 | August | 2 | 13 | 27438.5 | 28500 | 96.28%
[29 empty] | 2020 | August | 2 | 14 | 21832 | 28500 | 76.6%
[29 empty] | 2020 | August | 2 | 15 | 17094.5 | 28500 | 59.98%
[29 empty] | 2020 | August | 2 | 16 | 19833.5 | 28500 | 69.59%
[29 empty] | 2020 | August | 2 | 17 | 6788.5 | 28500 | 23.82%
[29 empty] | 2020 | August | 2 | 18 | 918.5 | 28500 | 3.223%
[29 empty] | 2020 | August | 2 | 19 | 299 | 28500 | 1.049%
[29 empty] | 2020 | August | 2 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 2 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 2 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 2 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 3 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 3 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 3 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 3 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 3 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 3 | 5 | 586 | 28500 | 2.056%
[29 empty] | 2020 | August | 3 | 6 | 3241 | 28500 | 11.37%
[29 empty] | 2020 | August | 3 | 7 | 8908 | 28500 | 31.26%
[29 empty] | 2020 | August | 3 | 8 | 20992 | 28500 | 73.66%
[29 empty] | 2020 | August | 3 | 9 | 27971.5 | 28500 | 98.15%
[29 empty] | 2020 | August | 3 | 10 | 24841 | 28500 | 87.16%
[29 empty] | 2020 | August | 3 | 11 | 24142 | 28500 | 84.71%
[29 empty] | 2020 | August | 3 | 12 | 17653 | 28500 | 61.94%
[29 empty] | 2020 | August | 3 | 13 | 19734 | 28500 | 69.24%
[29 empty] | 2020 | August | 3 | 14 | 17569.5 | 28500 | 61.65%
[29 empty] | 2020 | August | 3 | 15 | 18899 | 28500 | 66.31%
[29 empty] | 2020 | August | 3 | 16 | 7569 | 28500 | 26.56%
[29 empty] | 2020 | August | 3 | 17 | 5899.5 | 28500 | 20.7%
[29 empty] | 2020 | August | 3 | 18 | 1670 | 28500 | 5.86%
[29 empty] | 2020 | August | 3 | 19 | 18 | 28500 | 0.06316%
[29 empty] | 2020 | August | 3 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 3 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 3 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 3 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 4 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 4 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 4 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 4 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 4 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 4 | 5 | 563 | 28500 | 1.975%
[29 empty] | 2020 | August | 4 | 6 | 2456.5 | 28500 | 8.619%
[29 empty] | 2020 | August | 4 | 7 | 11010 | 28500 | 38.63%
[29 empty] | 2020 | August | 4 | 8 | 20765 | 28500 | 72.86%
[29 empty] | 2020 | August | 4 | 9 | 26213.5 | 28500 | 91.98%
[29 empty] | 2020 | August | 4 | 10 | 30573.5 | 28500 | 107.3%
[29 empty] | 2020 | August | 4 | 11 | 33458 | 28500 | 117.4%
[29 empty] | 2020 | August | 4 | 12 | 24705.5 | 28500 | 86.69%
[29 empty] | 2020 | August | 4 | 13 | 10184 | 28500 | 35.73%
[29 empty] | 2020 | August | 4 | 14 | 34131.5 | 28500 | 119.8%
[29 empty] | 2020 | August | 4 | 15 | 28247.5 | 28500 | 99.11%
[29 empty] | 2020 | August | 4 | 16 | 13658 | 28500 | 47.92%
[29 empty] | 2020 | August | 4 | 17 | 9364 | 28500 | 32.86%
[29 empty] | 2020 | August | 4 | 18 | 1371 | 28500 | 4.811%
[29 empty] | 2020 | August | 4 | 19 | 276 | 28500 | 0.9684%
[29 empty] | 2020 | August | 4 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 4 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 4 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 4 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 5 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 5 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 5 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 5 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 5 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 5 | 5 | 467 | 28500 | 1.639%
[29 empty] | 2020 | August | 5 | 6 | 3006 | 28500 | 10.55%
[29 empty] | 2020 | August | 5 | 7 | 8795 | 28500 | 30.86%
[29 empty] | 2020 | August | 5 | 8 | 19835.5 | 28500 | 69.6%
[29 empty] | 2020 | August | 5 | 9 | 29497 | 28500 | 103.5%
[29 empty] | 2020 | August | 5 | 10 | 34857 | 28500 | 122.3%
[29 empty] | 2020 | August | 5 | 11 | 39299 | 28500 | 137.9%
[29 empty] | 2020 | August | 5 | 12 | 38594.5 | 28500 | 135.4%
[29 empty] | 2020 | August | 5 | 13 | 26297 | 28500 | 92.27%
[29 empty] | 2020 | August | 5 | 14 | 34517 | 28500 | 121.1%
[29 empty] | 2020 | August | 5 | 15 | 27464 | 28500 | 96.36%
[29 empty] | 2020 | August | 5 | 16 | 20026 | 28500 | 70.27%
[29 empty] | 2020 | August | 5 | 17 | 8418.5 | 28500 | 29.54%
[29 empty] | 2020 | August | 5 | 18 | 2367.5 | 28500 | 8.307%
[29 empty] | 2020 | August | 5 | 19 | 154.5 | 28500 | 0.5421%
[29 empty] | 2020 | August | 5 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 5 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 5 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 5 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 6 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 6 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 6 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 6 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 6 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 6 | 5 | 329 | 28500 | 1.154%
[29 empty] | 2020 | August | 6 | 6 | 2919 | 28500 | 10.24%
[29 empty] | 2020 | August | 6 | 7 | 5420.5 | 28500 | 19.02%
[29 empty] | 2020 | August | 6 | 8 | 4133.5 | 28500 | 14.5%
[29 empty] | 2020 | August | 6 | 9 | 10967 | 28500 | 38.48%
[29 empty] | 2020 | August | 6 | 10 | 17272.5 | 28500 | 60.61%
[29 empty] | 2020 | August | 6 | 11 | 15727 | 28500 | 55.18%
[29 empty] | 2020 | August | 6 | 12 | 34182.5 | 28500 | 119.9%
[29 empty] | 2020 | August | 6 | 13 | 20303.5 | 28500 | 71.24%
[29 empty] | 2020 | August | 6 | 14 | 16528.5 | 28500 | 57.99%
[29 empty] | 2020 | August | 6 | 15 | 25166.5 | 28500 | 88.3%
[29 empty] | 2020 | August | 6 | 16 | 17677 | 28500 | 62.02%
[29 empty] | 2020 | August | 6 | 17 | 8602.5 | 28500 | 30.18%
[29 empty] | 2020 | August | 6 | 18 | 1419 | 28500 | 4.979%
[29 empty] | 2020 | August | 6 | 19 | 194.5 | 28500 | 0.6825%
[29 empty] | 2020 | August | 6 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 6 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 6 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 6 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 7 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 7 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 7 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 7 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 7 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 7 | 5 | 443 | 28500 | 1.554%
[29 empty] | 2020 | August | 7 | 6 | 2386 | 28500 | 8.372%
[29 empty] | 2020 | August | 7 | 7 | 10693.5 | 28500 | 37.52%
[29 empty] | 2020 | August | 7 | 8 | 20082 | 28500 | 70.46%
[29 empty] | 2020 | August | 7 | 9 | 27261 | 28500 | 95.65%
[29 empty] | 2020 | August | 7 | 10 | 32068 | 28500 | 112.5%
[29 empty] | 2020 | August | 7 | 11 | 35831 | 28500 | 125.7%
[29 empty] | 2020 | August | 7 | 12 | 37257.5 | 28500 | 130.7%
[29 empty] | 2020 | August | 7 | 13 | 35501 | 28500 | 124.6%
[29 empty] | 2020 | August | 7 | 14 | 31086.5 | 28500 | 109.1%
[29 empty] | 2020 | August | 7 | 15 | 25461 | 28500 | 89.34%
[29 empty] | 2020 | August | 7 | 16 | 8642.5 | 28500 | 30.32%
[29 empty] | 2020 | August | 7 | 17 | 2408.5 | 28500 | 8.451%
[29 empty] | 2020 | August | 7 | 18 | 398.5 | 28500 | 1.398%
[29 empty] | 2020 | August | 7 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 7 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 7 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 7 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 7 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 8 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 8 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 8 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 8 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 8 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 8 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 8 | 6 | 663.5 | 28500 | 2.328%
[29 empty] | 2020 | August | 8 | 7 | 6996 | 28500 | 24.55%
[29 empty] | 2020 | August | 8 | 8 | 14447.5 | 28500 | 50.69%
[29 empty] | 2020 | August | 8 | 9 | 14468 | 28500 | 50.76%
[29 empty] | 2020 | August | 8 | 10 | 16778 | 28500 | 58.87%
[29 empty] | 2020 | August | 8 | 11 | 20796.5 | 28500 | 72.97%
[29 empty] | 2020 | August | 8 | 12 | 21538.5 | 28500 | 75.57%
[29 empty] | 2020 | August | 8 | 13 | 33865 | 28500 | 118.8%
[29 empty] | 2020 | August | 8 | 14 | 24679.5 | 28500 | 86.59%
[29 empty] | 2020 | August | 8 | 15 | 17456.5 | 28500 | 61.25%
[29 empty] | 2020 | August | 8 | 16 | 13308.5 | 28500 | 46.7%
[29 empty] | 2020 | August | 8 | 17 | 7734 | 28500 | 27.14%
[29 empty] | 2020 | August | 8 | 18 | 982.5 | 28500 | 3.447%
[29 empty] | 2020 | August | 8 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 8 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 8 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 8 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 8 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 9 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 9 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 9 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 9 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 9 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 9 | 5 | 353 | 28500 | 1.239%
[29 empty] | 2020 | August | 9 | 6 | 2814.5 | 28500 | 9.875%
[29 empty] | 2020 | August | 9 | 7 | 7634.5 | 28500 | 26.79%
[29 empty] | 2020 | August | 9 | 8 | 18832 | 28500 | 66.08%
[29 empty] | 2020 | August | 9 | 9 | 23349 | 28500 | 81.93%
[29 empty] | 2020 | August | 9 | 10 | 24589.5 | 28500 | 86.28%
[29 empty] | 2020 | August | 9 | 11 | 36721.5 | 28500 | 128.8%
[29 empty] | 2020 | August | 9 | 12 | 38338 | 28500 | 134.5%
[29 empty] | 2020 | August | 9 | 13 | 34298 | 28500 | 120.3%
[29 empty] | 2020 | August | 9 | 14 | 31261.5 | 28500 | 109.7%
[29 empty] | 2020 | August | 9 | 15 | 25898.5 | 28500 | 90.87%
[29 empty] | 2020 | August | 9 | 16 | 13726 | 28500 | 48.16%
[29 empty] | 2020 | August | 9 | 17 | 7355 | 28500 | 25.81%
[29 empty] | 2020 | August | 9 | 18 | 2014 | 28500 | 7.067%
[29 empty] | 2020 | August | 9 | 19 | 16 | 28500 | 0.05614%
[29 empty] | 2020 | August | 9 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 9 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 9 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 9 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 10 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 10 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 10 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 10 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 10 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 10 | 5 | 272.5 | 28500 | 0.9561%
[29 empty] | 2020 | August | 10 | 6 | 2727.5 | 28500 | 9.57%
[29 empty] | 2020 | August | 10 | 7 | 9558 | 28500 | 33.54%
[29 empty] | 2020 | August | 10 | 8 | 19254 | 28500 | 67.56%
[29 empty] | 2020 | August | 10 | 9 | 26062.5 | 28500 | 91.45%
[29 empty] | 2020 | August | 10 | 10 | 31259 | 28500 | 109.7%
[29 empty] | 2020 | August | 10 | 11 | 34533.5 | 28500 | 121.2%
[29 empty] | 2020 | August | 10 | 12 | 35126 | 28500 | 123.2%
[29 empty] | 2020 | August | 10 | 13 | 35225 | 28500 | 123.6%
[29 empty] | 2020 | August | 10 | 14 | 30362 | 28500 | 106.5%
[29 empty] | 2020 | August | 10 | 15 | 25118.5 | 28500 | 88.14%
[29 empty] | 2020 | August | 10 | 16 | 16965 | 28500 | 59.53%
[29 empty] | 2020 | August | 10 | 17 | 6680.5 | 28500 | 23.44%
[29 empty] | 2020 | August | 10 | 18 | 1946.5 | 28500 | 6.83%
[29 empty] | 2020 | August | 10 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 10 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 10 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 10 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 10 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 11 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 11 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 11 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 11 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 11 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 11 | 5 | 248 | 28500 | 0.8702%
[29 empty] | 2020 | August | 11 | 6 | 2685.5 | 28500 | 9.423%
[29 empty] | 2020 | August | 11 | 7 | 9673.5 | 28500 | 33.94%
[29 empty] | 2020 | August | 11 | 8 | 19814.5 | 28500 | 69.52%
[29 empty] | 2020 | August | 11 | 9 | 26767 | 28500 | 93.92%
[29 empty] | 2020 | August | 11 | 10 | 31817 | 28500 | 111.6%
[29 empty] | 2020 | August | 11 | 11 | 35181 | 28500 | 123.4%
[29 empty] | 2020 | August | 11 | 12 | 36249.5 | 28500 | 127.2%
[29 empty] | 2020 | August | 11 | 13 | 34456.5 | 28500 | 120.9%
[29 empty] | 2020 | August | 11 | 14 | 29848.5 | 28500 | 104.7%
[29 empty] | 2020 | August | 11 | 15 | 24191.5 | 28500 | 84.88%
[29 empty] | 2020 | August | 11 | 16 | 16814.5 | 28500 | 59%
[29 empty] | 2020 | August | 11 | 17 | 7132.5 | 28500 | 25.03%
[29 empty] | 2020 | August | 11 | 18 | 1745 | 28500 | 6.123%
[29 empty] | 2020 | August | 11 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 11 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 11 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 11 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 11 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 12 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 12 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 12 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 12 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 12 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 12 | 5 | 223.5 | 28500 | 0.7842%
[29 empty] | 2020 | August | 12 | 6 | 2192 | 28500 | 7.691%
[29 empty] | 2020 | August | 12 | 7 | 7609 | 28500 | 26.7%
[29 empty] | 2020 | August | 12 | 8 | 18094.5 | 28500 | 63.49%
[29 empty] | 2020 | August | 12 | 9 | 25985 | 28500 | 91.18%
[29 empty] | 2020 | August | 12 | 10 | 31449 | 28500 | 110.3%
[29 empty] | 2020 | August | 12 | 11 | 34255.5 | 28500 | 120.2%
[29 empty] | 2020 | August | 12 | 12 | 35643.5 | 28500 | 125.1%
[29 empty] | 2020 | August | 12 | 13 | 32983 | 28500 | 115.7%
[29 empty] | 2020 | August | 12 | 14 | 23318 | 28500 | 81.82%
[29 empty] | 2020 | August | 12 | 15 | 13980 | 28500 | 49.05%
[29 empty] | 2020 | August | 12 | 16 | 16851.5 | 28500 | 59.13%
[29 empty] | 2020 | August | 12 | 17 | 7711.5 | 28500 | 27.06%
[29 empty] | 2020 | August | 12 | 18 | 1147 | 28500 | 4.025%
[29 empty] | 2020 | August | 12 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 12 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 12 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 12 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 12 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 13 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 13 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 13 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 13 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 13 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 13 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 13 | 6 | 2212.5 | 28500 | 7.763%
[29 empty] | 2020 | August | 13 | 7 | 9119 | 28500 | 32%
[29 empty] | 2020 | August | 13 | 8 | 18320.5 | 28500 | 64.28%
[29 empty] | 2020 | August | 13 | 9 | 26028 | 28500 | 91.33%
[29 empty] | 2020 | August | 13 | 10 | 32195.5 | 28500 | 113%
[29 empty] | 2020 | August | 13 | 11 | 33314 | 28500 | 116.9%
[29 empty] | 2020 | August | 13 | 12 | 16110 | 28500 | 56.53%
[29 empty] | 2020 | August | 13 | 13 | 7756 | 28500 | 27.21%
[29 empty] | 2020 | August | 13 | 14 | 1599 | 28500 | 5.611%
[29 empty] | 2020 | August | 13 | 15 | 3030 | 28500 | 10.63%
[29 empty] | 2020 | August | 13 | 16 | 9643.5 | 28500 | 33.84%
[29 empty] | 2020 | August | 13 | 17 | 3627.5 | 28500 | 12.73%
[29 empty] | 2020 | August | 13 | 18 | 1726.5 | 28500 | 6.058%
[29 empty] | 2020 | August | 13 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 13 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 13 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 13 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 13 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 14 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 14 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 14 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 14 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 14 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 14 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 14 | 6 | 428 | 28500 | 1.502%
[29 empty] | 2020 | August | 14 | 7 | 2436.5 | 28500 | 8.549%
[29 empty] | 2020 | August | 14 | 8 | 4250 | 28500 | 14.91%
[29 empty] | 2020 | August | 14 | 9 | 3899 | 28500 | 13.68%
[29 empty] | 2020 | August | 14 | 10 | 7115 | 28500 | 24.96%
[29 empty] | 2020 | August | 14 | 11 | 4697 | 28500 | 16.48%
[29 empty] | 2020 | August | 14 | 12 | 10517 | 28500 | 36.9%
[29 empty] | 2020 | August | 14 | 13 | 4927 | 28500 | 17.29%
[29 empty] | 2020 | August | 14 | 14 | 4061 | 28500 | 14.25%
[29 empty] | 2020 | August | 14 | 15 | 3534 | 28500 | 12.4%
[29 empty] | 2020 | August | 14 | 16 | 12024.5 | 28500 | 42.19%
[29 empty] | 2020 | August | 14 | 17 | 5795 | 28500 | 20.33%
[29 empty] | 2020 | August | 14 | 18 | 1734 | 28500 | 6.084%
[29 empty] | 2020 | August | 14 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 14 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 14 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 14 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 14 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 15 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 15 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 15 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 15 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 15 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 15 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 15 | 6 | 956.5 | 28500 | 3.356%
[29 empty] | 2020 | August | 15 | 7 | 2318 | 28500 | 8.133%
[29 empty] | 2020 | August | 15 | 8 | 3456 | 28500 | 12.13%
[29 empty] | 2020 | August | 15 | 9 | 4575 | 28500 | 16.05%
[29 empty] | 2020 | August | 15 | 10 | 4302 | 28500 | 15.09%
[29 empty] | 2020 | August | 15 | 11 | 3723.5 | 28500 | 13.06%
[29 empty] | 2020 | August | 15 | 12 | 2356.5 | 28500 | 8.268%
[29 empty] | 2020 | August | 15 | 13 | 1849 | 28500 | 6.488%
[29 empty] | 2020 | August | 15 | 14 | 2490 | 28500 | 8.737%
[29 empty] | 2020 | August | 15 | 15 | 10119.5 | 28500 | 35.51%
[29 empty] | 2020 | August | 15 | 16 | 3519 | 28500 | 12.35%
[29 empty] | 2020 | August | 15 | 17 | 1863 | 28500 | 6.537%
[29 empty] | 2020 | August | 15 | 18 | 539.5 | 28500 | 1.893%
[29 empty] | 2020 | August | 15 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 15 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 15 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 15 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 15 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 16 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 16 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 16 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 16 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 16 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 16 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 16 | 6 | 135.5 | 28500 | 0.4754%
[29 empty] | 2020 | August | 16 | 7 | 990.5 | 28500 | 3.475%
[29 empty] | 2020 | August | 16 | 8 | 5357.5 | 28500 | 18.8%
[29 empty] | 2020 | August | 16 | 9 | 10293 | 28500 | 36.12%
[29 empty] | 2020 | August | 16 | 10 | 17086 | 28500 | 59.95%
[29 empty] | 2020 | August | 16 | 11 | 13781 | 28500 | 48.35%
[29 empty] | 2020 | August | 16 | 12 | 10046.5 | 28500 | 35.25%
[29 empty] | 2020 | August | 16 | 13 | 5623.5 | 28500 | 19.73%
[29 empty] | 2020 | August | 16 | 14 | 2614 | 28500 | 9.172%
[29 empty] | 2020 | August | 16 | 15 | 6555 | 28500 | 23%
[29 empty] | 2020 | August | 16 | 16 | 9865.5 | 28500 | 34.62%
[29 empty] | 2020 | August | 16 | 17 | 8152.5 | 28500 | 28.61%
[29 empty] | 2020 | August | 16 | 18 | 1327 | 28500 | 4.656%
[29 empty] | 2020 | August | 16 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 16 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 16 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 16 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 16 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 17 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 17 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 17 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 17 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 17 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 17 | 5 | 19 | 28500 | 0.06667%
[29 empty] | 2020 | August | 17 | 6 | 2119.5 | 28500 | 7.437%
[29 empty] | 2020 | August | 17 | 7 | 10172 | 28500 | 35.69%
[29 empty] | 2020 | August | 17 | 8 | 12477.5 | 28500 | 43.78%
[29 empty] | 2020 | August | 17 | 9 | 23744.5 | 28500 | 83.31%
[29 empty] | 2020 | August | 17 | 10 | 12923 | 28500 | 45.34%
[29 empty] | 2020 | August | 17 | 11 | 20656 | 28500 | 72.48%
[29 empty] | 2020 | August | 17 | 12 | 19042.5 | 28500 | 66.82%
[29 empty] | 2020 | August | 17 | 13 | 30952.5 | 28500 | 108.6%
[29 empty] | 2020 | August | 17 | 14 | 12196 | 28500 | 42.79%
[29 empty] | 2020 | August | 17 | 15 | 5403 | 28500 | 18.96%
[29 empty] | 2020 | August | 17 | 16 | 14429 | 28500 | 50.63%
[29 empty] | 2020 | August | 17 | 17 | 7862.5 | 28500 | 27.59%
[29 empty] | 2020 | August | 17 | 18 | 1405 | 28500 | 4.93%
[29 empty] | 2020 | August | 17 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 17 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 17 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 17 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 17 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 18 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 18 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 18 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 18 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 18 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 18 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 18 | 6 | 2180 | 28500 | 7.649%
[29 empty] | 2020 | August | 18 | 7 | 10400.5 | 28500 | 36.49%
[29 empty] | 2020 | August | 18 | 8 | 17546.5 | 28500 | 61.57%
[29 empty] | 2020 | August | 18 | 9 | 24138.5 | 28500 | 84.7%
[29 empty] | 2020 | August | 18 | 10 | 16974.5 | 28500 | 59.56%
[29 empty] | 2020 | August | 18 | 11 | 19176.5 | 28500 | 67.29%
[29 empty] | 2020 | August | 18 | 12 | 27204 | 28500 | 95.45%
[29 empty] | 2020 | August | 18 | 13 | 15363.5 | 28500 | 53.91%
[29 empty] | 2020 | August | 18 | 14 | 24052 | 28500 | 84.39%
[29 empty] | 2020 | August | 18 | 15 | 25459 | 28500 | 89.33%
[29 empty] | 2020 | August | 18 | 16 | 17332.5 | 28500 | 60.82%
[29 empty] | 2020 | August | 18 | 17 | 7704.5 | 28500 | 27.03%
[29 empty] | 2020 | August | 18 | 18 | 1380.5 | 28500 | 4.844%
[29 empty] | 2020 | August | 18 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 18 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 18 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 18 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 18 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 19 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 19 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 19 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 19 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 19 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 19 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 19 | 6 | 2230.5 | 28500 | 7.826%
[29 empty] | 2020 | August | 19 | 7 | 489 | 28500 | 1.716%
[29 empty] | 2020 | August | 19 | 8 | 2497.5 | 28500 | 8.763%
[29 empty] | 2020 | August | 19 | 9 | 2999 | 28500 | 10.52%
[29 empty] | 2020 | August | 19 | 10 | 2711.5 | 28500 | 9.514%
[29 empty] | 2020 | August | 19 | 11 | 4250 | 28500 | 14.91%
[29 empty] | 2020 | August | 19 | 12 | 5244 | 28500 | 18.4%
[29 empty] | 2020 | August | 19 | 13 | 3465 | 28500 | 12.16%
[29 empty] | 2020 | August | 19 | 14 | 3125 | 28500 | 10.96%
[29 empty] | 2020 | August | 19 | 15 | 6081 | 28500 | 21.34%
[29 empty] | 2020 | August | 19 | 16 | 3151.5 | 28500 | 11.06%
[29 empty] | 2020 | August | 19 | 17 | 2056 | 28500 | 7.214%
[29 empty] | 2020 | August | 19 | 18 | 284.5 | 28500 | 0.9982%
[29 empty] | 2020 | August | 19 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 19 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 19 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 19 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 19 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 20 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 20 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 20 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 20 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 20 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 20 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 20 | 6 | 1722 | 28500 | 6.042%
[29 empty] | 2020 | August | 20 | 7 | 10474 | 28500 | 36.75%
[29 empty] | 2020 | August | 20 | 8 | 17663.5 | 28500 | 61.98%
[29 empty] | 2020 | August | 20 | 9 | 11247 | 28500 | 39.46%
[29 empty] | 2020 | August | 20 | 10 | 33825.5 | 28500 | 118.7%
[29 empty] | 2020 | August | 20 | 11 | 28442.5 | 28500 | 99.8%
[29 empty] | 2020 | August | 20 | 12 | 34259.5 | 28500 | 120.2%
[29 empty] | 2020 | August | 20 | 13 | 38576.5 | 28500 | 135.4%
[29 empty] | 2020 | August | 20 | 14 | 32872 | 28500 | 115.3%
[29 empty] | 2020 | August | 20 | 15 | 24712 | 28500 | 86.71%
[29 empty] | 2020 | August | 20 | 16 | 17521 | 28500 | 61.48%
[29 empty] | 2020 | August | 20 | 17 | 7666.5 | 28500 | 26.9%
[29 empty] | 2020 | August | 20 | 18 | 998 | 28500 | 3.502%
[29 empty] | 2020 | August | 20 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 20 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 20 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 20 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 20 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 21 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 21 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 21 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 21 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 21 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 21 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 21 | 6 | 1233.5 | 28500 | 4.328%
[29 empty] | 2020 | August | 21 | 7 | 4086 | 28500 | 14.34%
[29 empty] | 2020 | August | 21 | 8 | 8887.5 | 28500 | 31.18%
[29 empty] | 2020 | August | 21 | 9 | 14002.5 | 28500 | 49.13%
[29 empty] | 2020 | August | 21 | 10 | 6621 | 28500 | 23.23%
[29 empty] | 2020 | August | 21 | 11 | 13275.5 | 28500 | 46.58%
[29 empty] | 2020 | August | 21 | 12 | 21653.5 | 28500 | 75.98%
[29 empty] | 2020 | August | 21 | 13 | 8944 | 28500 | 31.38%
[29 empty] | 2020 | August | 21 | 14 | 11881.5 | 28500 | 41.69%
[29 empty] | 2020 | August | 21 | 15 | 17281.5 | 28500 | 60.64%
[29 empty] | 2020 | August | 21 | 16 | 14395 | 28500 | 50.51%
[29 empty] | 2020 | August | 21 | 17 | 7115 | 28500 | 24.96%
[29 empty] | 2020 | August | 21 | 18 | 1046.5 | 28500 | 3.672%
[29 empty] | 2020 | August | 21 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 21 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 21 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 21 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 21 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 22 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 22 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 22 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 22 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 22 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 22 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 22 | 6 | 1988.5 | 28500 | 6.977%
[29 empty] | 2020 | August | 22 | 7 | 9642 | 28500 | 33.83%
[29 empty] | 2020 | August | 22 | 8 | 14907 | 28500 | 52.31%
[29 empty] | 2020 | August | 22 | 9 | 16207 | 28500 | 56.87%
[29 empty] | 2020 | August | 22 | 10 | 33359.5 | 28500 | 117.1%
[29 empty] | 2020 | August | 22 | 11 | 29731.5 | 28500 | 104.3%
[29 empty] | 2020 | August | 22 | 12 | 39744 | 28500 | 139.5%
[29 empty] | 2020 | August | 22 | 13 | 12256.5 | 28500 | 43.01%
[29 empty] | 2020 | August | 22 | 14 | 28497.5 | 28500 | 99.99%
[29 empty] | 2020 | August | 22 | 15 | 21449 | 28500 | 75.26%
[29 empty] | 2020 | August | 22 | 16 | 12548.5 | 28500 | 44.03%
[29 empty] | 2020 | August | 22 | 17 | 6111 | 28500 | 21.44%
[29 empty] | 2020 | August | 22 | 18 | 1235 | 28500 | 4.333%
[29 empty] | 2020 | August | 22 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 22 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 22 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 22 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 22 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 23 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 23 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 23 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 23 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 23 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 23 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 23 | 6 | 2092.5 | 28500 | 7.342%
[29 empty] | 2020 | August | 23 | 7 | 9757 | 28500 | 34.24%
[29 empty] | 2020 | August | 23 | 8 | 15169 | 28500 | 53.22%
[29 empty] | 2020 | August | 23 | 9 | 13523 | 28500 | 47.45%
[29 empty] | 2020 | August | 23 | 10 | 11942 | 28500 | 41.9%
[29 empty] | 2020 | August | 23 | 11 | 9510 | 28500 | 33.37%
[29 empty] | 2020 | August | 23 | 12 | 15429.5 | 28500 | 54.14%
[29 empty] | 2020 | August | 23 | 13 | 16208.5 | 28500 | 56.87%
[29 empty] | 2020 | August | 23 | 14 | 8193 | 28500 | 28.75%
[29 empty] | 2020 | August | 23 | 15 | 20803 | 28500 | 72.99%
[29 empty] | 2020 | August | 23 | 16 | 14856 | 28500 | 52.13%
[29 empty] | 2020 | August | 23 | 17 | 5765.5 | 28500 | 20.23%
[29 empty] | 2020 | August | 23 | 18 | 1029 | 28500 | 3.611%
[29 empty] | 2020 | August | 23 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 23 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 23 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 23 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 23 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 24 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 24 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 24 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 24 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 24 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 24 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 24 | 6 | 1521.5 | 28500 | 5.339%
[29 empty] | 2020 | August | 24 | 7 | 4685.5 | 28500 | 16.44%
[29 empty] | 2020 | August | 24 | 8 | 19603.5 | 28500 | 68.78%
[29 empty] | 2020 | August | 24 | 9 | 17557 | 28500 | 61.6%
[29 empty] | 2020 | August | 24 | 10 | 17314 | 28500 | 60.75%
[29 empty] | 2020 | August | 24 | 11 | 26590 | 28500 | 93.3%
[29 empty] | 2020 | August | 24 | 12 | 22292.5 | 28500 | 78.22%
[29 empty] | 2020 | August | 24 | 13 | 19309 | 28500 | 67.75%
[29 empty] | 2020 | August | 24 | 14 | 24873 | 28500 | 87.27%
[29 empty] | 2020 | August | 24 | 15 | 6278 | 28500 | 22.03%
[29 empty] | 2020 | August | 24 | 16 | 4291 | 28500 | 15.06%
[29 empty] | 2020 | August | 24 | 17 | 3442 | 28500 | 12.08%
[29 empty] | 2020 | August | 24 | 18 | 548 | 28500 | 1.923%
[29 empty] | 2020 | August | 24 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 24 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 24 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 24 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 24 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 25 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 25 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 25 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 25 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 25 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 25 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 25 | 6 | 907 | 28500 | 3.182%
[29 empty] | 2020 | August | 25 | 7 | 3926 | 28500 | 13.78%
[29 empty] | 2020 | August | 25 | 8 | 7877.5 | 28500 | 27.64%
[29 empty] | 2020 | August | 25 | 9 | 13940.5 | 28500 | 48.91%
[29 empty] | 2020 | August | 25 | 10 | 10333 | 28500 | 36.26%
[29 empty] | 2020 | August | 25 | 11 | 12473.5 | 28500 | 43.77%
[29 empty] | 2020 | August | 25 | 12 | 10259 | 28500 | 36%
[29 empty] | 2020 | August | 25 | 13 | 17865 | 28500 | 62.68%
[29 empty] | 2020 | August | 25 | 14 | 27434 | 28500 | 96.26%
[29 empty] | 2020 | August | 25 | 15 | 19087.5 | 28500 | 66.97%
[29 empty] | 2020 | August | 25 | 16 | 16049 | 28500 | 56.31%
[29 empty] | 2020 | August | 25 | 17 | 6286.5 | 28500 | 22.06%
[29 empty] | 2020 | August | 25 | 18 | 893.5 | 28500 | 3.135%
[29 empty] | 2020 | August | 25 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 25 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 25 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 25 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 25 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 26 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 26 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 26 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 26 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 26 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 26 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 26 | 6 | 1945.5 | 28500 | 6.826%
[29 empty] | 2020 | August | 26 | 7 | 9912 | 28500 | 34.78%
[29 empty] | 2020 | August | 26 | 8 | 20619.5 | 28500 | 72.35%
[29 empty] | 2020 | August | 26 | 9 | 17924.5 | 28500 | 62.89%
[29 empty] | 2020 | August | 26 | 10 | 16195 | 28500 | 56.82%
[29 empty] | 2020 | August | 26 | 11 | 36861.5 | 28500 | 129.3%
[29 empty] | 2020 | August | 26 | 12 | 34431.5 | 28500 | 120.8%
[29 empty] | 2020 | August | 26 | 13 | 12215.5 | 28500 | 42.86%
[29 empty] | 2020 | August | 26 | 14 | 14075.5 | 28500 | 49.39%
[29 empty] | 2020 | August | 26 | 15 | 10069 | 28500 | 35.33%
[29 empty] | 2020 | August | 26 | 16 | 8045 | 28500 | 28.23%
[29 empty] | 2020 | August | 26 | 17 | 4855.5 | 28500 | 17.04%
[29 empty] | 2020 | August | 26 | 18 | 802.5 | 28500 | 2.816%
[29 empty] | 2020 | August | 26 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 26 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 26 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 26 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 26 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 27 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 27 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 27 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 27 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 27 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 27 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 27 | 6 | 1877.5 | 28500 | 6.588%
[29 empty] | 2020 | August | 27 | 7 | 7867.5 | 28500 | 27.61%
[29 empty] | 2020 | August | 27 | 8 | 19134 | 28500 | 67.14%
[29 empty] | 2020 | August | 27 | 9 | 11883.5 | 28500 | 41.7%
[29 empty] | 2020 | August | 27 | 10 | 7513 | 28500 | 26.36%
[29 empty] | 2020 | August | 27 | 11 | 4833 | 28500 | 16.96%
[29 empty] | 2020 | August | 27 | 12 | 4604 | 28500 | 16.15%
[29 empty] | 2020 | August | 27 | 13 | 3297.5 | 28500 | 11.57%
[29 empty] | 2020 | August | 27 | 14 | 8333.5 | 28500 | 29.24%
[29 empty] | 2020 | August | 27 | 15 | 1173 | 28500 | 4.116%
[29 empty] | 2020 | August | 27 | 16 | 5922.5 | 28500 | 20.78%
[29 empty] | 2020 | August | 27 | 17 | 5318.5 | 28500 | 18.66%
[29 empty] | 2020 | August | 27 | 18 | 3 | 28500 | 0.01053%
[29 empty] | 2020 | August | 27 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 27 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 27 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 27 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 27 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 28 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 28 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 28 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 28 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 28 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 28 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 28 | 6 | 1767 | 28500 | 6.2%
[29 empty] | 2020 | August | 28 | 7 | 7136.5 | 28500 | 25.04%
[29 empty] | 2020 | August | 28 | 8 | 7710 | 28500 | 27.05%
[29 empty] | 2020 | August | 28 | 9 | 6396 | 28500 | 22.44%
[29 empty] | 2020 | August | 28 | 10 | 26851.5 | 28500 | 94.22%
[29 empty] | 2020 | August | 28 | 11 | 27369.5 | 28500 | 96.03%
[29 empty] | 2020 | August | 28 | 12 | 10223.5 | 28500 | 35.87%
[29 empty] | 2020 | August | 28 | 13 | 13101 | 28500 | 45.97%
[29 empty] | 2020 | August | 28 | 14 | 4235.5 | 28500 | 14.86%
[29 empty] | 2020 | August | 28 | 15 | 8004.5 | 28500 | 28.09%
[29 empty] | 2020 | August | 28 | 16 | 3994.5 | 28500 | 14.02%
[29 empty] | 2020 | August | 28 | 17 | 3655 | 28500 | 12.82%
[29 empty] | 2020 | August | 28 | 18 | 116.5 | 28500 | 0.4088%
[29 empty] | 2020 | August | 28 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 28 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 28 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 28 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 28 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 29 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 29 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 29 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 29 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 29 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 29 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 29 | 6 | 50.5 | 28500 | 0.1772%
[29 empty] | 2020 | August | 29 | 7 | 3008.5 | 28500 | 10.56%
[29 empty] | 2020 | August | 29 | 8 | 2543.5 | 28500 | 8.925%
[29 empty] | 2020 | August | 29 | 9 | 1795.5 | 28500 | 6.3%
[29 empty] | 2020 | August | 29 | 10 | 7054 | 28500 | 24.75%
[29 empty] | 2020 | August | 29 | 11 | 9091.5 | 28500 | 31.9%
[29 empty] | 2020 | August | 29 | 12 | 8271.5 | 28500 | 29.02%
[29 empty] | 2020 | August | 29 | 13 | 3832.5 | 28500 | 13.45%
[29 empty] | 2020 | August | 29 | 14 | 3677.5 | 28500 | 12.9%
[29 empty] | 2020 | August | 29 | 15 | 5458.5 | 28500 | 19.15%
[29 empty] | 2020 | August | 29 | 16 | 6351 | 28500 | 22.28%
[29 empty] | 2020 | August | 29 | 17 | 3372.5 | 28500 | 11.83%
[29 empty] | 2020 | August | 29 | 18 | 645.5 | 28500 | 2.265%
[29 empty] | 2020 | August | 29 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 29 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 29 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 29 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 29 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 30 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 30 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 30 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 30 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 30 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 30 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 30 | 6 | 725 | 28500 | 2.544%
[29 empty] | 2020 | August | 30 | 7 | 3931.5 | 28500 | 13.79%
[29 empty] | 2020 | August | 30 | 8 | 8954.5 | 28500 | 31.42%
[29 empty] | 2020 | August | 30 | 9 | 22397.5 | 28500 | 78.59%
[29 empty] | 2020 | August | 30 | 10 | 15025 | 28500 | 52.72%
[29 empty] | 2020 | August | 30 | 11 | 6026 | 28500 | 21.14%
[29 empty] | 2020 | August | 30 | 12 | 4512.5 | 28500 | 15.83%
[29 empty] | 2020 | August | 30 | 13 | 5857.5 | 28500 | 20.55%
[29 empty] | 2020 | August | 30 | 14 | 14427 | 28500 | 50.62%
[29 empty] | 2020 | August | 30 | 15 | 9810 | 28500 | 34.42%
[29 empty] | 2020 | August | 30 | 16 | 9017 | 28500 | 31.64%
[29 empty] | 2020 | August | 30 | 17 | 3526 | 28500 | 12.37%
[29 empty] | 2020 | August | 30 | 18 | 609.5 | 28500 | 2.139%
[29 empty] | 2020 | August | 30 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 30 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 30 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 30 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 30 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 31 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 31 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 31 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 31 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 31 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 31 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 31 | 6 | 1608 | 28500 | 5.642%
[29 empty] | 2020 | August | 31 | 7 | 8992 | 28500 | 31.55%
[29 empty] | 2020 | August | 31 | 8 | 16629.5 | 28500 | 58.35%
[29 empty] | 2020 | August | 31 | 9 | 27343 | 28500 | 95.94%
[29 empty] | 2020 | August | 31 | 10 | 13303 | 28500 | 46.68%
[29 empty] | 2020 | August | 31 | 11 | 15625 | 28500 | 54.82%
[29 empty] | 2020 | August | 31 | 12 | 24370.5 | 28500 | 85.51%
[29 empty] | 2020 | August | 31 | 13 | 22541.5 | 28500 | 79.09%
[29 empty] | 2020 | August | 31 | 14 | 5195.5 | 28500 | 18.23%
[29 empty] | 2020 | August | 31 | 15 | 18781.5 | 28500 | 65.9%
[29 empty] | 2020 | August | 31 | 16 | 7815.5 | 28500 | 27.42%
[29 empty] | 2020 | August | 31 | 17 | 4587.5 | 28500 | 16.1%
[29 empty] | 2020 | August | 31 | 18 | 551.5 | 28500 | 1.935%
[29 empty] | 2020 | August | 31 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 31 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 31 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 31 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | August | 31 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 1 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 1 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 1 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 1 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 1 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 1 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 1 | 6 | 1574.5 | 28500 | 5.525%
[29 empty] | 2020 | September | 1 | 7 | 10385 | 28500 | 36.44%
[29 empty] | 2020 | September | 1 | 8 | 20934.5 | 28500 | 73.45%
[29 empty] | 2020 | September | 1 | 9 | 29575.5 | 28500 | 103.8%
[29 empty] | 2020 | September | 1 | 10 | 31462 | 28500 | 110.4%
[29 empty] | 2020 | September | 1 | 11 | 30051 | 28500 | 105.4%
[29 empty] | 2020 | September | 1 | 12 | 28467.5 | 28500 | 99.89%
[29 empty] | 2020 | September | 1 | 13 | 20566 | 28500 | 72.16%
[29 empty] | 2020 | September | 1 | 14 | 10526 | 28500 | 36.93%
[29 empty] | 2020 | September | 1 | 15 | 15368.5 | 28500 | 53.92%
[29 empty] | 2020 | September | 1 | 16 | 8482.5 | 28500 | 29.76%
[29 empty] | 2020 | September | 1 | 17 | 3697 | 28500 | 12.97%
[29 empty] | 2020 | September | 1 | 18 | 279.5 | 28500 | 0.9807%
[29 empty] | 2020 | September | 1 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 1 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 1 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 1 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 1 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 2 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 2 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 2 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 2 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 2 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 2 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 2 | 6 | 1568 | 28500 | 5.502%
[29 empty] | 2020 | September | 2 | 7 | 9991 | 28500 | 35.06%
[29 empty] | 2020 | September | 2 | 8 | 20099 | 28500 | 70.52%
[29 empty] | 2020 | September | 2 | 9 | 27885.5 | 28500 | 97.84%
[29 empty] | 2020 | September | 2 | 10 | 32381 | 28500 | 113.6%
[29 empty] | 2020 | September | 2 | 11 | 21778 | 28500 | 76.41%
[29 empty] | 2020 | September | 2 | 12 | 13872 | 28500 | 48.67%
[29 empty] | 2020 | September | 2 | 13 | 16879.5 | 28500 | 59.23%
[29 empty] | 2020 | September | 2 | 14 | 10108 | 28500 | 35.47%
[29 empty] | 2020 | September | 2 | 15 | 3661 | 28500 | 12.85%
[29 empty] | 2020 | September | 2 | 16 | 3215.5 | 28500 | 11.28%
[29 empty] | 2020 | September | 2 | 17 | 1235.5 | 28500 | 4.335%
[29 empty] | 2020 | September | 2 | 18 | 230.5 | 28500 | 0.8088%
[29 empty] | 2020 | September | 2 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 2 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 2 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 2 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 2 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 3 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 3 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 3 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 3 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 3 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 3 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 3 | 6 | 1399 | 28500 | 4.909%
[29 empty] | 2020 | September | 3 | 7 | 866.5 | 28500 | 3.04%
[29 empty] | 2020 | September | 3 | 8 | 1895.5 | 28500 | 6.651%
[29 empty] | 2020 | September | 3 | 9 | 11009 | 28500 | 38.63%
[29 empty] | 2020 | September | 3 | 10 | 11695.5 | 28500 | 41.04%
[29 empty] | 2020 | September | 3 | 11 | 7430.5 | 28500 | 26.07%
[29 empty] | 2020 | September | 3 | 12 | 6272 | 28500 | 22.01%
[29 empty] | 2020 | September | 3 | 13 | 12539.5 | 28500 | 44%
[29 empty] | 2020 | September | 3 | 14 | 12924.5 | 28500 | 45.35%
[29 empty] | 2020 | September | 3 | 15 | 11330 | 28500 | 39.75%
[29 empty] | 2020 | September | 3 | 16 | 3127 | 28500 | 10.97%
[29 empty] | 2020 | September | 3 | 17 | 3198 | 28500 | 11.22%
[29 empty] | 2020 | September | 3 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 3 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 3 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 3 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 3 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 3 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 4 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 4 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 4 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 4 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 4 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 4 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 4 | 6 | 1405.5 | 28500 | 4.932%
[29 empty] | 2020 | September | 4 | 7 | 7260.5 | 28500 | 25.48%
[29 empty] | 2020 | September | 4 | 8 | 15775 | 28500 | 55.35%
[29 empty] | 2020 | September | 4 | 9 | 9224.5 | 28500 | 32.37%
[29 empty] | 2020 | September | 4 | 10 | 19419.5 | 28500 | 68.14%
[29 empty] | 2020 | September | 4 | 11 | 19452.5 | 28500 | 68.25%
[29 empty] | 2020 | September | 4 | 12 | 13217 | 28500 | 46.38%
[29 empty] | 2020 | September | 4 | 13 | 18547.5 | 28500 | 65.08%
[29 empty] | 2020 | September | 4 | 14 | 5663.5 | 28500 | 19.87%
[29 empty] | 2020 | September | 4 | 15 | 8935.5 | 28500 | 31.35%
[29 empty] | 2020 | September | 4 | 16 | 4526.5 | 28500 | 15.88%
[29 empty] | 2020 | September | 4 | 17 | 2071.5 | 28500 | 7.268%
[29 empty] | 2020 | September | 4 | 18 | 135.5 | 28500 | 0.4754%
[29 empty] | 2020 | September | 4 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 4 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 4 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 4 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 4 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 5 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 5 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 5 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 5 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 5 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 5 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 5 | 6 | 1442.5 | 28500 | 5.061%
[29 empty] | 2020 | September | 5 | 7 | 10413.5 | 28500 | 36.54%
[29 empty] | 2020 | September | 5 | 8 | 20897.5 | 28500 | 73.32%
[29 empty] | 2020 | September | 5 | 9 | 22232.5 | 28500 | 78.01%
[29 empty] | 2020 | September | 5 | 10 | 32647 | 28500 | 114.6%
[29 empty] | 2020 | September | 5 | 11 | 19384 | 28500 | 68.01%
[29 empty] | 2020 | September | 5 | 12 | 17129.5 | 28500 | 60.1%
[29 empty] | 2020 | September | 5 | 13 | 26562.5 | 28500 | 93.2%
[29 empty] | 2020 | September | 5 | 14 | 32740.5 | 28500 | 114.9%
[29 empty] | 2020 | September | 5 | 15 | 7738 | 28500 | 27.15%
[29 empty] | 2020 | September | 5 | 16 | 10578 | 28500 | 37.12%
[29 empty] | 2020 | September | 5 | 17 | 5104.5 | 28500 | 17.91%
[29 empty] | 2020 | September | 5 | 18 | 137 | 28500 | 0.4807%
[29 empty] | 2020 | September | 5 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 5 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 5 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 5 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 5 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 6 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 6 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 6 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 6 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 6 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 6 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 6 | 6 | 1357.5 | 28500 | 4.763%
[29 empty] | 2020 | September | 6 | 7 | 4496 | 28500 | 15.78%
[29 empty] | 2020 | September | 6 | 8 | 18731.5 | 28500 | 65.72%
[29 empty] | 2020 | September | 6 | 9 | 29105.5 | 28500 | 102.1%
[29 empty] | 2020 | September | 6 | 10 | 34568 | 28500 | 121.3%
[29 empty] | 2020 | September | 6 | 11 | 33212 | 28500 | 116.5%
[29 empty] | 2020 | September | 6 | 12 | 11774 | 28500 | 41.31%
[29 empty] | 2020 | September | 6 | 13 | 17434.5 | 28500 | 61.17%
[29 empty] | 2020 | September | 6 | 14 | 6655.5 | 28500 | 23.35%
[29 empty] | 2020 | September | 6 | 15 | 14007 | 28500 | 49.15%
[29 empty] | 2020 | September | 6 | 16 | 15794 | 28500 | 55.42%
[29 empty] | 2020 | September | 6 | 17 | 5331 | 28500 | 18.71%
[29 empty] | 2020 | September | 6 | 18 | 136 | 28500 | 0.4772%
[29 empty] | 2020 | September | 6 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 6 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 6 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 6 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 6 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 7 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 7 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 7 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 7 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 7 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 7 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 7 | 6 | 1298 | 28500 | 4.554%
[29 empty] | 2020 | September | 7 | 7 | 3249 | 28500 | 11.4%
[29 empty] | 2020 | September | 7 | 8 | 3879 | 28500 | 13.61%
[29 empty] | 2020 | September | 7 | 9 | 5377 | 28500 | 18.87%
[29 empty] | 2020 | September | 7 | 10 | 25749.5 | 28500 | 90.35%
[29 empty] | 2020 | September | 7 | 11 | 16778.5 | 28500 | 58.87%
[29 empty] | 2020 | September | 7 | 12 | 11146.5 | 28500 | 39.11%
[29 empty] | 2020 | September | 7 | 13 | 8102 | 28500 | 28.43%
[29 empty] | 2020 | September | 7 | 14 | 11753.5 | 28500 | 41.24%
[29 empty] | 2020 | September | 7 | 15 | 14644 | 28500 | 51.38%
[29 empty] | 2020 | September | 7 | 16 | 6575.5 | 28500 | 23.07%
[29 empty] | 2020 | September | 7 | 17 | 4442.5 | 28500 | 15.59%
[29 empty] | 2020 | September | 7 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 7 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 7 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 7 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 7 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 7 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 8 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 8 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 8 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 8 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 8 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 8 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 8 | 6 | 852.5 | 28500 | 2.991%
[29 empty] | 2020 | September | 8 | 7 | 2709.5 | 28500 | 9.507%
[29 empty] | 2020 | September | 8 | 8 | 7957 | 28500 | 27.92%
[29 empty] | 2020 | September | 8 | 9 | 9871.5 | 28500 | 34.64%
[29 empty] | 2020 | September | 8 | 10 | 11387 | 28500 | 39.95%
[29 empty] | 2020 | September | 8 | 11 | 23565.5 | 28500 | 82.69%
[29 empty] | 2020 | September | 8 | 12 | 21045 | 28500 | 73.84%
[29 empty] | 2020 | September | 8 | 13 | 23651 | 28500 | 82.99%
[29 empty] | 2020 | September | 8 | 14 | 12289.5 | 28500 | 43.12%
[29 empty] | 2020 | September | 8 | 15 | 13496 | 28500 | 47.35%
[29 empty] | 2020 | September | 8 | 16 | 7234.5 | 28500 | 25.38%
[29 empty] | 2020 | September | 8 | 17 | 2111 | 28500 | 7.407%
[29 empty] | 2020 | September | 8 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 8 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 8 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 8 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 8 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 8 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 9 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 9 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 9 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 9 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 9 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 9 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 9 | 6 | 1151.5 | 28500 | 4.04%
[29 empty] | 2020 | September | 9 | 7 | 8193.5 | 28500 | 28.75%
[29 empty] | 2020 | September | 9 | 8 | 16655 | 28500 | 58.44%
[29 empty] | 2020 | September | 9 | 9 | 15217 | 28500 | 53.39%
[29 empty] | 2020 | September | 9 | 10 | 23231.5 | 28500 | 81.51%
[29 empty] | 2020 | September | 9 | 11 | 17086 | 28500 | 59.95%
[29 empty] | 2020 | September | 9 | 12 | 6136.5 | 28500 | 21.53%
[29 empty] | 2020 | September | 9 | 13 | 11298.5 | 28500 | 39.64%
[29 empty] | 2020 | September | 9 | 14 | 17140 | 28500 | 60.14%
[29 empty] | 2020 | September | 9 | 15 | 7498.5 | 28500 | 26.31%
[29 empty] | 2020 | September | 9 | 16 | 4138.5 | 28500 | 14.52%
[29 empty] | 2020 | September | 9 | 17 | 1640 | 28500 | 5.754%
[29 empty] | 2020 | September | 9 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 9 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 9 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 9 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 9 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 9 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 10 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 10 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 10 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 10 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 10 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 10 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 10 | 6 | 1173.5 | 28500 | 4.118%
[29 empty] | 2020 | September | 10 | 7 | 10008 | 28500 | 35.12%
[29 empty] | 2020 | September | 10 | 8 | 20225 | 28500 | 70.96%
[29 empty] | 2020 | September | 10 | 9 | 28327.5 | 28500 | 99.39%
[29 empty] | 2020 | September | 10 | 10 | 23813.5 | 28500 | 83.56%
[29 empty] | 2020 | September | 10 | 11 | 27205 | 28500 | 95.46%
[29 empty] | 2020 | September | 10 | 12 | 34420.5 | 28500 | 120.8%
[29 empty] | 2020 | September | 10 | 13 | 25310 | 28500 | 88.81%
[29 empty] | 2020 | September | 10 | 14 | 18643.5 | 28500 | 65.42%
[29 empty] | 2020 | September | 10 | 15 | 19070.5 | 28500 | 66.91%
[29 empty] | 2020 | September | 10 | 16 | 9966.5 | 28500 | 34.97%
[29 empty] | 2020 | September | 10 | 17 | 3637.5 | 28500 | 12.76%
[29 empty] | 2020 | September | 10 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 10 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 10 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 10 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 10 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 10 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 11 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 11 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 11 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 11 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 11 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 11 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 11 | 6 | 841.5 | 28500 | 2.953%
[29 empty] | 2020 | September | 11 | 7 | 5350 | 28500 | 18.77%
[29 empty] | 2020 | September | 11 | 8 | 11042.5 | 28500 | 38.75%
[29 empty] | 2020 | September | 11 | 9 | 14109.5 | 28500 | 49.51%
[29 empty] | 2020 | September | 11 | 10 | 18761 | 28500 | 65.83%
[29 empty] | 2020 | September | 11 | 11 | 30972 | 28500 | 108.7%
[29 empty] | 2020 | September | 11 | 12 | 38272 | 28500 | 134.3%
[29 empty] | 2020 | September | 11 | 13 | 32317.5 | 28500 | 113.4%
[29 empty] | 2020 | September | 11 | 14 | 30663.5 | 28500 | 107.6%
[29 empty] | 2020 | September | 11 | 15 | 22041 | 28500 | 77.34%
[29 empty] | 2020 | September | 11 | 16 | 13593 | 28500 | 47.69%
[29 empty] | 2020 | September | 11 | 17 | 4014.5 | 28500 | 14.09%
[29 empty] | 2020 | September | 11 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 11 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 11 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 11 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 11 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 11 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 12 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 12 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 12 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 12 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 12 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 12 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 12 | 6 | 937 | 28500 | 3.288%
[29 empty] | 2020 | September | 12 | 7 | 8743 | 28500 | 30.68%
[29 empty] | 2020 | September | 12 | 8 | 19590 | 28500 | 68.74%
[29 empty] | 2020 | September | 12 | 9 | 10411.5 | 28500 | 36.53%
[29 empty] | 2020 | September | 12 | 10 | 15585 | 28500 | 54.68%
[29 empty] | 2020 | September | 12 | 11 | 21313 | 28500 | 74.78%
[29 empty] | 2020 | September | 12 | 12 | 28253.5 | 28500 | 99.14%
[29 empty] | 2020 | September | 12 | 13 | 22700 | 28500 | 79.65%
[29 empty] | 2020 | September | 12 | 14 | 25833.5 | 28500 | 90.64%
[29 empty] | 2020 | September | 12 | 15 | 23390.5 | 28500 | 82.07%
[29 empty] | 2020 | September | 12 | 16 | 12856.5 | 28500 | 45.11%
[29 empty] | 2020 | September | 12 | 17 | 3528 | 28500 | 12.38%
[29 empty] | 2020 | September | 12 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 12 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 12 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 12 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 12 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 12 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 13 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 13 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 13 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 13 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 13 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 13 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 13 | 6 | 800 | 28500 | 2.807%
[29 empty] | 2020 | September | 13 | 7 | 8765 | 28500 | 30.75%
[29 empty] | 2020 | September | 13 | 8 | 19465.5 | 28500 | 68.3%
[29 empty] | 2020 | September | 13 | 9 | 28145 | 28500 | 98.75%
[29 empty] | 2020 | September | 13 | 10 | 35985.5 | 28500 | 126.3%
[29 empty] | 2020 | September | 13 | 11 | 38325 | 28500 | 134.5%
[29 empty] | 2020 | September | 13 | 12 | 40474.5 | 28500 | 142%
[29 empty] | 2020 | September | 13 | 13 | 35254.5 | 28500 | 123.7%
[29 empty] | 2020 | September | 13 | 14 | 31140.5 | 28500 | 109.3%
[29 empty] | 2020 | September | 13 | 15 | 25028 | 28500 | 87.82%
[29 empty] | 2020 | September | 13 | 16 | 14463.5 | 28500 | 50.75%
[29 empty] | 2020 | September | 13 | 17 | 3721 | 28500 | 13.06%
[29 empty] | 2020 | September | 13 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 13 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 13 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 13 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 13 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 13 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 14 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 14 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 14 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 14 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 14 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 14 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 14 | 6 | 687.5 | 28500 | 2.412%
[29 empty] | 2020 | September | 14 | 7 | 8530.5 | 28500 | 29.93%
[29 empty] | 2020 | September | 14 | 8 | 19156.5 | 28500 | 67.22%
[29 empty] | 2020 | September | 14 | 9 | 27621 | 28500 | 96.92%
[29 empty] | 2020 | September | 14 | 10 | 34793 | 28500 | 122.1%
[29 empty] | 2020 | September | 14 | 11 | 36963.5 | 28500 | 129.7%
[29 empty] | 2020 | September | 14 | 12 | 38237 | 28500 | 134.2%
[29 empty] | 2020 | September | 14 | 13 | 34607.5 | 28500 | 121.4%
[29 empty] | 2020 | September | 14 | 14 | 30404.5 | 28500 | 106.7%
[29 empty] | 2020 | September | 14 | 15 | 23755 | 28500 | 83.35%
[29 empty] | 2020 | September | 14 | 16 | 14212.5 | 28500 | 49.87%
[29 empty] | 2020 | September | 14 | 17 | 3793.5 | 28500 | 13.31%
[29 empty] | 2020 | September | 14 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 14 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 14 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 14 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 14 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 14 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 15 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 15 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 15 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 15 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 15 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 15 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 15 | 6 | 532 | 28500 | 1.867%
[29 empty] | 2020 | September | 15 | 7 | 6541 | 28500 | 22.95%
[29 empty] | 2020 | September | 15 | 8 | 14965.5 | 28500 | 52.51%
[29 empty] | 2020 | September | 15 | 9 | 26178 | 28500 | 91.85%
[29 empty] | 2020 | September | 15 | 10 | 32205.5 | 28500 | 113%
[29 empty] | 2020 | September | 15 | 11 | 34769 | 28500 | 122%
[29 empty] | 2020 | September | 15 | 12 | 22114 | 28500 | 77.59%
[29 empty] | 2020 | September | 15 | 13 | 31858 | 28500 | 111.8%
[29 empty] | 2020 | September | 15 | 14 | 26608 | 28500 | 93.36%
[29 empty] | 2020 | September | 15 | 15 | 14773.5 | 28500 | 51.84%
[29 empty] | 2020 | September | 15 | 16 | 13597.5 | 28500 | 47.71%
[29 empty] | 2020 | September | 15 | 17 | 3083.5 | 28500 | 10.82%
[29 empty] | 2020 | September | 15 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 15 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 15 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 15 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 15 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 15 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 16 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 16 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 16 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 16 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 16 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 16 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 16 | 6 | 426 | 28500 | 1.495%
[29 empty] | 2020 | September | 16 | 7 | 2780.5 | 28500 | 9.756%
[29 empty] | 2020 | September | 16 | 8 | 6326 | 28500 | 22.2%
[29 empty] | 2020 | September | 16 | 9 | 7042.5 | 28500 | 24.71%
[29 empty] | 2020 | September | 16 | 10 | 9693.5 | 28500 | 34.01%
[29 empty] | 2020 | September | 16 | 11 | 6839 | 28500 | 24%
[29 empty] | 2020 | September | 16 | 12 | 9986 | 28500 | 35.04%
[29 empty] | 2020 | September | 16 | 13 | 28744.5 | 28500 | 100.9%
[29 empty] | 2020 | September | 16 | 14 | 15705 | 28500 | 55.11%
[29 empty] | 2020 | September | 16 | 15 | 17841 | 28500 | 62.6%
[29 empty] | 2020 | September | 16 | 16 | 12712.5 | 28500 | 44.61%
[29 empty] | 2020 | September | 16 | 17 | 3053.5 | 28500 | 10.71%
[29 empty] | 2020 | September | 16 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 16 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 16 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 16 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 16 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 16 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 17 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 17 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 17 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 17 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 17 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 17 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 17 | 6 | 446.5 | 28500 | 1.567%
[29 empty] | 2020 | September | 17 | 7 | 7305 | 28500 | 25.63%
[29 empty] | 2020 | September | 17 | 8 | 15760 | 28500 | 55.3%
[29 empty] | 2020 | September | 17 | 9 | 26247.5 | 28500 | 92.1%
[29 empty] | 2020 | September | 17 | 10 | 32326.5 | 28500 | 113.4%
[29 empty] | 2020 | September | 17 | 11 | 36986 | 28500 | 129.8%
[29 empty] | 2020 | September | 17 | 12 | 38094.5 | 28500 | 133.7%
[29 empty] | 2020 | September | 17 | 13 | 35737 | 28500 | 125.4%
[29 empty] | 2020 | September | 17 | 14 | 31970.5 | 28500 | 112.2%
[29 empty] | 2020 | September | 17 | 15 | 23687.5 | 28500 | 83.11%
[29 empty] | 2020 | September | 17 | 16 | 13310 | 28500 | 46.7%
[29 empty] | 2020 | September | 17 | 17 | 3279.5 | 28500 | 11.51%
[29 empty] | 2020 | September | 17 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 17 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 17 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 17 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 17 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 17 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 18 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 18 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 18 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 18 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 18 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 18 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 18 | 6 | 521 | 28500 | 1.828%
[29 empty] | 2020 | September | 18 | 7 | 8626.5 | 28500 | 30.27%
[29 empty] | 2020 | September | 18 | 8 | 20008 | 28500 | 70.2%
[29 empty] | 2020 | September | 18 | 9 | 28413.5 | 28500 | 99.7%
[29 empty] | 2020 | September | 18 | 10 | 36256.5 | 28500 | 127.2%
[29 empty] | 2020 | September | 18 | 11 | 39441.5 | 28500 | 138.4%
[29 empty] | 2020 | September | 18 | 12 | 41077 | 28500 | 144.1%
[29 empty] | 2020 | September | 18 | 13 | 37255 | 28500 | 130.7%
[29 empty] | 2020 | September | 18 | 14 | 32074 | 28500 | 112.5%
[29 empty] | 2020 | September | 18 | 15 | 24604 | 28500 | 86.33%
[29 empty] | 2020 | September | 18 | 16 | 7620 | 28500 | 26.74%
[29 empty] | 2020 | September | 18 | 17 | 3542.5 | 28500 | 12.43%
[29 empty] | 2020 | September | 18 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 18 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 18 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 18 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 18 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 18 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 19 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 19 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 19 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 19 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 19 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 19 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 19 | 6 | 226.5 | 28500 | 0.7947%
[29 empty] | 2020 | September | 19 | 7 | 6032.5 | 28500 | 21.17%
[29 empty] | 2020 | September | 19 | 8 | 16673.5 | 28500 | 58.5%
[29 empty] | 2020 | September | 19 | 9 | 26638 | 28500 | 93.47%
[29 empty] | 2020 | September | 19 | 10 | 33671.5 | 28500 | 118.1%
[29 empty] | 2020 | September | 19 | 11 | 35561 | 28500 | 124.8%
[29 empty] | 2020 | September | 19 | 12 | 25392.5 | 28500 | 89.1%
[29 empty] | 2020 | September | 19 | 13 | 26537 | 28500 | 93.11%
[29 empty] | 2020 | September | 19 | 14 | 26179.5 | 28500 | 91.86%
[29 empty] | 2020 | September | 19 | 15 | 19006.5 | 28500 | 66.69%
[29 empty] | 2020 | September | 19 | 16 | 7820 | 28500 | 27.44%
[29 empty] | 2020 | September | 19 | 17 | 2833.5 | 28500 | 9.942%
[29 empty] | 2020 | September | 19 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 19 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 19 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 19 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 19 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 19 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 20 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 20 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 20 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 20 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 20 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 20 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 20 | 6 | 339.5 | 28500 | 1.191%
[29 empty] | 2020 | September | 20 | 7 | 5856.5 | 28500 | 20.55%
[29 empty] | 2020 | September | 20 | 8 | 18137 | 28500 | 63.64%
[29 empty] | 2020 | September | 20 | 9 | 27162.5 | 28500 | 95.31%
[29 empty] | 2020 | September | 20 | 10 | 33592 | 28500 | 117.9%
[29 empty] | 2020 | September | 20 | 11 | 36790.5 | 28500 | 129.1%
[29 empty] | 2020 | September | 20 | 12 | 36848.5 | 28500 | 129.3%
[29 empty] | 2020 | September | 20 | 13 | 33725.5 | 28500 | 118.3%
[29 empty] | 2020 | September | 20 | 14 | 15337 | 28500 | 53.81%
[29 empty] | 2020 | September | 20 | 15 | 21587.5 | 28500 | 75.75%
[29 empty] | 2020 | September | 20 | 16 | 12035.5 | 28500 | 42.23%
[29 empty] | 2020 | September | 20 | 17 | 2536.5 | 28500 | 8.9%
[29 empty] | 2020 | September | 20 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 20 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 20 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 20 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 20 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 20 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 21 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 21 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 21 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 21 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 21 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 21 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 21 | 6 | 50.5 | 28500 | 0.1772%
[29 empty] | 2020 | September | 21 | 7 | 2564.5 | 28500 | 8.998%
[29 empty] | 2020 | September | 21 | 8 | 4648.5 | 28500 | 16.31%
[29 empty] | 2020 | September | 21 | 9 | 4512 | 28500 | 15.83%
[29 empty] | 2020 | September | 21 | 10 | 9471 | 28500 | 33.23%
[29 empty] | 2020 | September | 21 | 11 | 32854.5 | 28500 | 115.3%
[29 empty] | 2020 | September | 21 | 12 | 36037.5 | 28500 | 126.4%
[29 empty] | 2020 | September | 21 | 13 | 33787.5 | 28500 | 118.6%
[29 empty] | 2020 | September | 21 | 14 | 29291.5 | 28500 | 102.8%
[29 empty] | 2020 | September | 21 | 15 | 21456 | 28500 | 75.28%
[29 empty] | 2020 | September | 21 | 16 | 12060.5 | 28500 | 42.32%
[29 empty] | 2020 | September | 21 | 17 | 2552.5 | 28500 | 8.956%
[29 empty] | 2020 | September | 21 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 21 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 21 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 21 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 21 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 21 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 22 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 22 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 22 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 22 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 22 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 22 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 22 | 6 | 251.5 | 28500 | 0.8825%
[29 empty] | 2020 | September | 22 | 7 | 6338.5 | 28500 | 22.24%
[29 empty] | 2020 | September | 22 | 8 | 17925.5 | 28500 | 62.9%
[29 empty] | 2020 | September | 22 | 9 | 26583.5 | 28500 | 93.28%
[29 empty] | 2020 | September | 22 | 10 | 31157.5 | 28500 | 109.3%
[29 empty] | 2020 | September | 22 | 11 | 34879.5 | 28500 | 122.4%
[29 empty] | 2020 | September | 22 | 12 | 31528 | 28500 | 110.6%
[29 empty] | 2020 | September | 22 | 13 | 34307.5 | 28500 | 120.4%
[29 empty] | 2020 | September | 22 | 14 | 29627 | 28500 | 104%
[29 empty] | 2020 | September | 22 | 15 | 20906.5 | 28500 | 73.36%
[29 empty] | 2020 | September | 22 | 16 | 9752 | 28500 | 34.22%
[29 empty] | 2020 | September | 22 | 17 | 1611 | 28500 | 5.653%
[29 empty] | 2020 | September | 22 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 22 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 22 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 22 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 22 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 22 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 23 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 23 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 23 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 23 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 23 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 23 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 23 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 23 | 7 | 1075 | 28500 | 3.772%
[29 empty] | 2020 | September | 23 | 8 | 5766.5 | 28500 | 20.23%
[29 empty] | 2020 | September | 23 | 9 | 17547.5 | 28500 | 61.57%
[29 empty] | 2020 | September | 23 | 10 | 9543.5 | 28500 | 33.49%
[29 empty] | 2020 | September | 23 | 11 | 5779.5 | 28500 | 20.28%
[29 empty] | 2020 | September | 23 | 12 | 12233 | 28500 | 42.92%
[29 empty] | 2020 | September | 23 | 13 | 12458.5 | 28500 | 43.71%
[29 empty] | 2020 | September | 23 | 14 | 7048.5 | 28500 | 24.73%
[29 empty] | 2020 | September | 23 | 15 | 2037.5 | 28500 | 7.149%
[29 empty] | 2020 | September | 23 | 16 | 6969 | 28500 | 24.45%
[29 empty] | 2020 | September | 23 | 17 | 1359.5 | 28500 | 4.77%
[29 empty] | 2020 | September | 23 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 23 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 23 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 23 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 23 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 23 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 24 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 24 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 24 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 24 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 24 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 24 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 24 | 6 | 157 | 28500 | 0.5509%
[29 empty] | 2020 | September | 24 | 7 | 7463.5 | 28500 | 26.19%
[29 empty] | 2020 | September | 24 | 8 | 19745 | 28500 | 69.28%
[29 empty] | 2020 | September | 24 | 9 | 27236 | 28500 | 95.56%
[29 empty] | 2020 | September | 24 | 10 | 35546 | 28500 | 124.7%
[29 empty] | 2020 | September | 24 | 11 | 27006.5 | 28500 | 94.76%
[29 empty] | 2020 | September | 24 | 12 | 35138 | 28500 | 123.3%
[29 empty] | 2020 | September | 24 | 13 | 20332.5 | 28500 | 71.34%
[29 empty] | 2020 | September | 24 | 14 | 4734.5 | 28500 | 16.61%
[29 empty] | 2020 | September | 24 | 15 | 2458.5 | 28500 | 8.626%
[29 empty] | 2020 | September | 24 | 16 | 791.5 | 28500 | 2.777%
[29 empty] | 2020 | September | 24 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 24 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 24 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 24 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 24 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 24 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 24 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 25 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 25 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 25 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 25 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 25 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 25 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 25 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 25 | 7 | 170 | 28500 | 0.5965%
[29 empty] | 2020 | September | 25 | 8 | 3691.5 | 28500 | 12.95%
[29 empty] | 2020 | September | 25 | 9 | 9900.5 | 28500 | 34.74%
[29 empty] | 2020 | September | 25 | 10 | 13420 | 28500 | 47.09%
[29 empty] | 2020 | September | 25 | 11 | 8255.5 | 28500 | 28.97%
[29 empty] | 2020 | September | 25 | 12 | 4382.5 | 28500 | 15.38%
[29 empty] | 2020 | September | 25 | 13 | 3478 | 28500 | 12.2%
[29 empty] | 2020 | September | 25 | 14 | 5789.5 | 28500 | 20.31%
[29 empty] | 2020 | September | 25 | 15 | 20865 | 28500 | 73.21%
[29 empty] | 2020 | September | 25 | 16 | 10936 | 28500 | 38.37%
[29 empty] | 2020 | September | 25 | 17 | 1724 | 28500 | 6.049%
[29 empty] | 2020 | September | 25 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 25 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 25 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 25 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 25 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 25 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 26 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 26 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 26 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 26 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 26 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 26 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 26 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 26 | 7 | 8372.5 | 28500 | 29.38%
[29 empty] | 2020 | September | 26 | 8 | 20359 | 28500 | 71.44%
[29 empty] | 2020 | September | 26 | 9 | 29044 | 28500 | 101.9%
[29 empty] | 2020 | September | 26 | 10 | 28671.5 | 28500 | 100.6%
[29 empty] | 2020 | September | 26 | 11 | 7012.5 | 28500 | 24.61%
[29 empty] | 2020 | September | 26 | 12 | 4595.5 | 28500 | 16.12%
[29 empty] | 2020 | September | 26 | 13 | 3741.5 | 28500 | 13.13%
[29 empty] | 2020 | September | 26 | 14 | 10404 | 28500 | 36.51%
[29 empty] | 2020 | September | 26 | 15 | 3019 | 28500 | 10.59%
[29 empty] | 2020 | September | 26 | 16 | 2188.5 | 28500 | 7.679%
[29 empty] | 2020 | September | 26 | 17 | 31.5 | 28500 | 0.1105%
[29 empty] | 2020 | September | 26 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 26 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 26 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 26 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 26 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 26 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 27 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 27 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 27 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 27 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 27 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 27 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 27 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 27 | 7 | 1716.5 | 28500 | 6.023%
[29 empty] | 2020 | September | 27 | 8 | 2422.5 | 28500 | 8.5%
[29 empty] | 2020 | September | 27 | 9 | 2907 | 28500 | 10.2%
[29 empty] | 2020 | September | 27 | 10 | 2100 | 28500 | 7.368%
[29 empty] | 2020 | September | 27 | 11 | 2571.5 | 28500 | 9.023%
[29 empty] | 2020 | September | 27 | 12 | 1357.5 | 28500 | 4.763%
[29 empty] | 2020 | September | 27 | 13 | 1253.5 | 28500 | 4.398%
[29 empty] | 2020 | September | 27 | 14 | 1713 | 28500 | 6.011%
[29 empty] | 2020 | September | 27 | 15 | 1894.5 | 28500 | 6.647%
[29 empty] | 2020 | September | 27 | 16 | 782.5 | 28500 | 2.746%
[29 empty] | 2020 | September | 27 | 17 | 395 | 28500 | 1.386%
[29 empty] | 2020 | September | 27 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 27 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 27 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 27 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 27 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 27 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 28 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 28 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 28 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 28 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 28 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 28 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 28 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 28 | 7 | 5158 | 28500 | 18.1%
[29 empty] | 2020 | September | 28 | 8 | 10716 | 28500 | 37.6%
[29 empty] | 2020 | September | 28 | 9 | 19491 | 28500 | 68.39%
[29 empty] | 2020 | September | 28 | 10 | 30077 | 28500 | 105.5%
[29 empty] | 2020 | September | 28 | 11 | 34501.5 | 28500 | 121.1%
[29 empty] | 2020 | September | 28 | 12 | 36713 | 28500 | 128.8%
[29 empty] | 2020 | September | 28 | 13 | 34160 | 28500 | 119.9%
[29 empty] | 2020 | September | 28 | 14 | 29397 | 28500 | 103.1%
[29 empty] | 2020 | September | 28 | 15 | 20578.5 | 28500 | 72.21%
[29 empty] | 2020 | September | 28 | 16 | 6449 | 28500 | 22.63%
[29 empty] | 2020 | September | 28 | 17 | 755.5 | 28500 | 2.651%
[29 empty] | 2020 | September | 28 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 28 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 28 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 28 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 28 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 28 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 29 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 29 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 29 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 29 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 29 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 29 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 29 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 29 | 7 | 2882.5 | 28500 | 10.11%
[29 empty] | 2020 | September | 29 | 8 | 1849 | 28500 | 6.488%
[29 empty] | 2020 | September | 29 | 9 | 2725.5 | 28500 | 9.563%
[29 empty] | 2020 | September | 29 | 10 | 9853.5 | 28500 | 34.57%
[29 empty] | 2020 | September | 29 | 11 | 3785.5 | 28500 | 13.28%
[29 empty] | 2020 | September | 29 | 12 | 3940.5 | 28500 | 13.83%
[29 empty] | 2020 | September | 29 | 13 | 15236.5 | 28500 | 53.46%
[29 empty] | 2020 | September | 29 | 14 | 13589 | 28500 | 47.68%
[29 empty] | 2020 | September | 29 | 15 | 11497 | 28500 | 40.34%
[29 empty] | 2020 | September | 29 | 16 | 9869 | 28500 | 34.63%
[29 empty] | 2020 | September | 29 | 17 | 1044 | 28500 | 3.663%
[29 empty] | 2020 | September | 29 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 29 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 29 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 29 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 29 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 29 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 30 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 30 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 30 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 30 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 30 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 30 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 30 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 30 | 7 | 6188.5 | 28500 | 21.71%
[29 empty] | 2020 | September | 30 | 8 | 7599.5 | 28500 | 26.66%
[29 empty] | 2020 | September | 30 | 9 | 4300.5 | 28500 | 15.09%
[29 empty] | 2020 | September | 30 | 10 | 9042.5 | 28500 | 31.73%
[29 empty] | 2020 | September | 30 | 11 | 13922 | 28500 | 48.85%
[29 empty] | 2020 | September | 30 | 12 | 2338 | 28500 | 8.204%
[29 empty] | 2020 | September | 30 | 13 | 5877 | 28500 | 20.62%
[29 empty] | 2020 | September | 30 | 14 | 2201.5 | 28500 | 7.725%
[29 empty] | 2020 | September | 30 | 15 | 2841.5 | 28500 | 9.97%
[29 empty] | 2020 | September | 30 | 16 | 5459.5 | 28500 | 19.16%
[29 empty] | 2020 | September | 30 | 17 | 365 | 28500 | 1.281%
[29 empty] | 2020 | September | 30 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 30 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 30 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 30 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 30 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | September | 30 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 1 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 1 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 1 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 1 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 1 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 1 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 1 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 1 | 7 | 539 | 28500 | 1.891%
[29 empty] | 2020 | October | 1 | 8 | 17948 | 28500 | 62.98%
[29 empty] | 2020 | October | 1 | 9 | 4449.5 | 28500 | 15.61%
[29 empty] | 2020 | October | 1 | 10 | 5179 | 28500 | 18.17%
[29 empty] | 2020 | October | 1 | 11 | 8719.5 | 28500 | 30.59%
[29 empty] | 2020 | October | 1 | 12 | 16796.5 | 28500 | 58.94%
[29 empty] | 2020 | October | 1 | 13 | 13688 | 28500 | 48.03%
[29 empty] | 2020 | October | 1 | 14 | 13268.5 | 28500 | 46.56%
[29 empty] | 2020 | October | 1 | 15 | 17755.5 | 28500 | 62.3%
[29 empty] | 2020 | October | 1 | 16 | 8713 | 28500 | 30.57%
[29 empty] | 2020 | October | 1 | 17 | 318.5 | 28500 | 1.118%
[29 empty] | 2020 | October | 1 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 1 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 1 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 1 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 1 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 1 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 2 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 2 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 2 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 2 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 2 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 2 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 2 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 2 | 7 | 244.5 | 28500 | 0.8579%
[29 empty] | 2020 | October | 2 | 8 | 1485.5 | 28500 | 5.212%
[29 empty] | 2020 | October | 2 | 9 | 2033 | 28500 | 7.133%
[29 empty] | 2020 | October | 2 | 10 | 2970 | 28500 | 10.42%
[29 empty] | 2020 | October | 2 | 11 | 3233.5 | 28500 | 11.35%
[29 empty] | 2020 | October | 2 | 12 | 2581.5 | 28500 | 9.058%
[29 empty] | 2020 | October | 2 | 13 | 1874.5 | 28500 | 6.577%
[29 empty] | 2020 | October | 2 | 14 | 1691 | 28500 | 5.933%
[29 empty] | 2020 | October | 2 | 15 | 1654.5 | 28500 | 5.805%
[29 empty] | 2020 | October | 2 | 16 | 755.5 | 28500 | 2.651%
[29 empty] | 2020 | October | 2 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 2 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 2 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 2 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 2 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 2 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 2 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 3 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 3 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 3 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 3 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 3 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 3 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 3 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 3 | 7 | 242 | 28500 | 0.8491%
[29 empty] | 2020 | October | 3 | 8 | 1122 | 28500 | 3.937%
[29 empty] | 2020 | October | 3 | 9 | 1435 | 28500 | 5.035%
[29 empty] | 2020 | October | 3 | 10 | 10527 | 28500 | 36.94%
[29 empty] | 2020 | October | 3 | 11 | 5033.5 | 28500 | 17.66%
[29 empty] | 2020 | October | 3 | 12 | 9884.5 | 28500 | 34.68%
[29 empty] | 2020 | October | 3 | 13 | 10127 | 28500 | 35.53%
[29 empty] | 2020 | October | 3 | 14 | 5394 | 28500 | 18.93%
[29 empty] | 2020 | October | 3 | 15 | 8759 | 28500 | 30.73%
[29 empty] | 2020 | October | 3 | 16 | 850 | 28500 | 2.982%
[29 empty] | 2020 | October | 3 | 17 | 50 | 28500 | 0.1754%
[29 empty] | 2020 | October | 3 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 3 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 3 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 3 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 3 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 3 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 4 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 4 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 4 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 4 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 4 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 4 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 4 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 4 | 7 | 333 | 28500 | 1.168%
[29 empty] | 2020 | October | 4 | 8 | 1397 | 28500 | 4.902%
[29 empty] | 2020 | October | 4 | 9 | 4755 | 28500 | 16.68%
[29 empty] | 2020 | October | 4 | 10 | 4340 | 28500 | 15.23%
[29 empty] | 2020 | October | 4 | 11 | 4691 | 28500 | 16.46%
[29 empty] | 2020 | October | 4 | 12 | 3543 | 28500 | 12.43%
[29 empty] | 2020 | October | 4 | 13 | 5594.5 | 28500 | 19.63%
[29 empty] | 2020 | October | 4 | 14 | 2536 | 28500 | 8.898%
[29 empty] | 2020 | October | 4 | 15 | 2652.5 | 28500 | 9.307%
[29 empty] | 2020 | October | 4 | 16 | 193.5 | 28500 | 0.6789%
[29 empty] | 2020 | October | 4 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 4 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 4 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 4 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 4 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 4 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 4 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 5 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 5 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 5 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 5 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 5 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 5 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 5 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 5 | 7 | 705.5 | 28500 | 2.475%
[29 empty] | 2020 | October | 5 | 8 | 8834 | 28500 | 31%
[29 empty] | 2020 | October | 5 | 9 | 7597.5 | 28500 | 26.66%
[29 empty] | 2020 | October | 5 | 10 | 32516 | 28500 | 114.1%
[29 empty] | 2020 | October | 5 | 11 | 34589.5 | 28500 | 121.4%
[29 empty] | 2020 | October | 5 | 12 | 25856 | 28500 | 90.72%
[29 empty] | 2020 | October | 5 | 13 | 16238 | 28500 | 56.98%
[29 empty] | 2020 | October | 5 | 14 | 8123 | 28500 | 28.5%
[29 empty] | 2020 | October | 5 | 15 | 3322 | 28500 | 11.66%
[29 empty] | 2020 | October | 5 | 16 | 2191 | 28500 | 7.688%
[29 empty] | 2020 | October | 5 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 5 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 5 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 5 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 5 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 5 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 5 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 6 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 6 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 6 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 6 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 6 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 6 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 6 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 6 | 7 | 6635.5 | 28500 | 23.28%
[29 empty] | 2020 | October | 6 | 8 | 13809 | 28500 | 48.45%
[29 empty] | 2020 | October | 6 | 9 | 24438 | 28500 | 85.75%
[29 empty] | 2020 | October | 6 | 10 | 7931.5 | 28500 | 27.83%
[29 empty] | 2020 | October | 6 | 11 | 8352.5 | 28500 | 29.31%
[29 empty] | 2020 | October | 6 | 12 | 8517.5 | 28500 | 29.89%
[29 empty] | 2020 | October | 6 | 13 | 15094.5 | 28500 | 52.96%
[29 empty] | 2020 | October | 6 | 14 | 25773.5 | 28500 | 90.43%
[29 empty] | 2020 | October | 6 | 15 | 8108.5 | 28500 | 28.45%
[29 empty] | 2020 | October | 6 | 16 | 3659.5 | 28500 | 12.84%
[29 empty] | 2020 | October | 6 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 6 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 6 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 6 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 6 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 6 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 6 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 7 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 7 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 7 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 7 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 7 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 7 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 7 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 7 | 7 | 1750.5 | 28500 | 6.142%
[29 empty] | 2020 | October | 7 | 8 | 7397.5 | 28500 | 25.96%
[29 empty] | 2020 | October | 7 | 9 | 11538.5 | 28500 | 40.49%
[29 empty] | 2020 | October | 7 | 10 | 30231 | 28500 | 106.1%
[29 empty] | 2020 | October | 7 | 11 | 26515.5 | 28500 | 93.04%
[29 empty] | 2020 | October | 7 | 12 | 23834.5 | 28500 | 83.63%
[29 empty] | 2020 | October | 7 | 13 | 28991.5 | 28500 | 101.7%
[29 empty] | 2020 | October | 7 | 14 | 20982 | 28500 | 73.62%
[29 empty] | 2020 | October | 7 | 15 | 13736 | 28500 | 48.2%
[29 empty] | 2020 | October | 7 | 16 | 4793 | 28500 | 16.82%
[29 empty] | 2020 | October | 7 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 7 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 7 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 7 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 7 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 7 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 7 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 8 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 8 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 8 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 8 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 8 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 8 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 8 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 8 | 7 | 1196.5 | 28500 | 4.198%
[29 empty] | 2020 | October | 8 | 8 | 5116 | 28500 | 17.95%
[29 empty] | 2020 | October | 8 | 9 | 4027.5 | 28500 | 14.13%
[29 empty] | 2020 | October | 8 | 10 | 7847.5 | 28500 | 27.54%
[29 empty] | 2020 | October | 8 | 11 | 2987 | 28500 | 10.48%
[29 empty] | 2020 | October | 8 | 12 | 2573 | 28500 | 9.028%
[29 empty] | 2020 | October | 8 | 13 | 7112.5 | 28500 | 24.96%
[29 empty] | 2020 | October | 8 | 14 | 9856 | 28500 | 34.58%
[29 empty] | 2020 | October | 8 | 15 | 14274.5 | 28500 | 50.09%
[29 empty] | 2020 | October | 8 | 16 | 1787 | 28500 | 6.27%
[29 empty] | 2020 | October | 8 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 8 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 8 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 8 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 8 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 8 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 8 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 9 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 9 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 9 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 9 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 9 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 9 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 9 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 9 | 7 | 5222 | 28500 | 18.32%
[29 empty] | 2020 | October | 9 | 8 | 16048.5 | 28500 | 56.31%
[29 empty] | 2020 | October | 9 | 9 | 26414.5 | 28500 | 92.68%
[29 empty] | 2020 | October | 9 | 10 | 32152.5 | 28500 | 112.8%
[29 empty] | 2020 | October | 9 | 11 | 34318 | 28500 | 120.4%
[29 empty] | 2020 | October | 9 | 12 | 12394.5 | 28500 | 43.49%
[29 empty] | 2020 | October | 9 | 13 | 7775 | 28500 | 27.28%
[29 empty] | 2020 | October | 9 | 14 | 6457 | 28500 | 22.66%
[29 empty] | 2020 | October | 9 | 15 | 4744 | 28500 | 16.65%
[29 empty] | 2020 | October | 9 | 16 | 2437.5 | 28500 | 8.553%
[29 empty] | 2020 | October | 9 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 9 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 9 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 9 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 9 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 9 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 9 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 10 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 10 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 10 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 10 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 10 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 10 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 10 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 10 | 7 | 4637 | 28500 | 16.27%
[29 empty] | 2020 | October | 10 | 8 | 15627 | 28500 | 54.83%
[29 empty] | 2020 | October | 10 | 9 | 12786 | 28500 | 44.86%
[29 empty] | 2020 | October | 10 | 10 | 7451 | 28500 | 26.14%
[29 empty] | 2020 | October | 10 | 11 | 11584.5 | 28500 | 40.65%
[29 empty] | 2020 | October | 10 | 12 | 3277 | 28500 | 11.5%
[29 empty] | 2020 | October | 10 | 13 | 1771 | 28500 | 6.214%
[29 empty] | 2020 | October | 10 | 14 | 4747.5 | 28500 | 16.66%
[29 empty] | 2020 | October | 10 | 15 | 2172 | 28500 | 7.621%
[29 empty] | 2020 | October | 10 | 16 | 2677.5 | 28500 | 9.395%
[29 empty] | 2020 | October | 10 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 10 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 10 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 10 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 10 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 10 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 10 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 11 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 11 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 11 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 11 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 11 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 11 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 11 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 11 | 7 | 3995 | 28500 | 14.02%
[29 empty] | 2020 | October | 11 | 8 | 17566 | 28500 | 61.64%
[29 empty] | 2020 | October | 11 | 9 | 17133 | 28500 | 60.12%
[29 empty] | 2020 | October | 11 | 10 | 30826 | 28500 | 108.2%
[29 empty] | 2020 | October | 11 | 11 | 8162 | 28500 | 28.64%
[29 empty] | 2020 | October | 11 | 12 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 11 | 13 | 6080 | 28500 | 21.33%
[29 empty] | 2020 | October | 11 | 14 | 8208 | 28500 | 28.8%
[29 empty] | 2020 | October | 11 | 15 | 7444 | 28500 | 26.12%
[29 empty] | 2020 | October | 11 | 16 | 2370.5 | 28500 | 8.318%
[29 empty] | 2020 | October | 11 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 11 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 11 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 11 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 11 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 11 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 11 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 12 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 12 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 12 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 12 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 12 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 12 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 12 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 12 | 7 | 2938.5 | 28500 | 10.31%
[29 empty] | 2020 | October | 12 | 8 | 1728.5 | 28500 | 6.065%
[29 empty] | 2020 | October | 12 | 9 | 2576 | 28500 | 9.039%
[29 empty] | 2020 | October | 12 | 10 | 8487 | 28500 | 29.78%
[29 empty] | 2020 | October | 12 | 11 | 8585.5 | 28500 | 30.12%
[29 empty] | 2020 | October | 12 | 12 | 6389 | 28500 | 22.42%
[29 empty] | 2020 | October | 12 | 13 | 9963 | 28500 | 34.96%
[29 empty] | 2020 | October | 12 | 14 | 725.5 | 28500 | 2.546%
[29 empty] | 2020 | October | 12 | 15 | 2721.5 | 28500 | 9.549%
[29 empty] | 2020 | October | 12 | 16 | 861 | 28500 | 3.021%
[29 empty] | 2020 | October | 12 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 12 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 12 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 12 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 12 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 12 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 12 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 13 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 13 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 13 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 13 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 13 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 13 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 13 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 13 | 7 | 4683 | 28500 | 16.43%
[29 empty] | 2020 | October | 13 | 8 | 4189.5 | 28500 | 14.7%
[29 empty] | 2020 | October | 13 | 9 | 1363.5 | 28500 | 4.784%
[29 empty] | 2020 | October | 13 | 10 | 3003 | 28500 | 10.54%
[29 empty] | 2020 | October | 13 | 11 | 4477.5 | 28500 | 15.71%
[29 empty] | 2020 | October | 13 | 12 | 1105 | 28500 | 3.877%
[29 empty] | 2020 | October | 13 | 13 | 966 | 28500 | 3.389%
[29 empty] | 2020 | October | 13 | 14 | 698.5 | 28500 | 2.451%
[29 empty] | 2020 | October | 13 | 15 | 1782.5 | 28500 | 6.254%
[29 empty] | 2020 | October | 13 | 16 | 219.5 | 28500 | 0.7702%
[29 empty] | 2020 | October | 13 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 13 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 13 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 13 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 13 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 13 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 13 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 14 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 14 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 14 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 14 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 14 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 14 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 14 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 14 | 7 | 2756.5 | 28500 | 9.672%
[29 empty] | 2020 | October | 14 | 8 | 5120.5 | 28500 | 17.97%
[29 empty] | 2020 | October | 14 | 9 | 25200.5 | 28500 | 88.42%
[29 empty] | 2020 | October | 14 | 10 | 12833 | 28500 | 45.03%
[29 empty] | 2020 | October | 14 | 11 | 8794.5 | 28500 | 30.86%
[29 empty] | 2020 | October | 14 | 12 | 5688.5 | 28500 | 19.96%
[29 empty] | 2020 | October | 14 | 13 | 5762.5 | 28500 | 20.22%
[29 empty] | 2020 | October | 14 | 14 | 8928 | 28500 | 31.33%
[29 empty] | 2020 | October | 14 | 15 | 3926.5 | 28500 | 13.78%
[29 empty] | 2020 | October | 14 | 16 | 1634 | 28500 | 5.733%
[29 empty] | 2020 | October | 14 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 14 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 14 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 14 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 14 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 14 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 14 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 15 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 15 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 15 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 15 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 15 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 15 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 15 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 15 | 7 | 5541.5 | 28500 | 19.44%
[29 empty] | 2020 | October | 15 | 8 | 6538.5 | 28500 | 22.94%
[29 empty] | 2020 | October | 15 | 9 | 11661.5 | 28500 | 40.92%
[29 empty] | 2020 | October | 15 | 10 | 11897 | 28500 | 41.74%
[29 empty] | 2020 | October | 15 | 11 | 12063 | 28500 | 42.33%
[29 empty] | 2020 | October | 15 | 12 | 14809 | 28500 | 51.96%
[29 empty] | 2020 | October | 15 | 13 | 29808.5 | 28500 | 104.6%
[29 empty] | 2020 | October | 15 | 14 | 7876 | 28500 | 27.64%
[29 empty] | 2020 | October | 15 | 15 | 4952 | 28500 | 17.38%
[29 empty] | 2020 | October | 15 | 16 | 3976 | 28500 | 13.95%
[29 empty] | 2020 | October | 15 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 15 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 15 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 15 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 15 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 15 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 15 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 16 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 16 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 16 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 16 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 16 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 16 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 16 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 16 | 7 | 1509.5 | 28500 | 5.296%
[29 empty] | 2020 | October | 16 | 8 | 3676 | 28500 | 12.9%
[29 empty] | 2020 | October | 16 | 9 | 2318 | 28500 | 8.133%
[29 empty] | 2020 | October | 16 | 10 | 4380.5 | 28500 | 15.37%
[29 empty] | 2020 | October | 16 | 11 | 8562 | 28500 | 30.04%
[29 empty] | 2020 | October | 16 | 12 | 6458 | 28500 | 22.66%
[29 empty] | 2020 | October | 16 | 13 | 4269.5 | 28500 | 14.98%
[29 empty] | 2020 | October | 16 | 14 | 1442 | 28500 | 5.06%
[29 empty] | 2020 | October | 16 | 15 | 3321 | 28500 | 11.65%
[29 empty] | 2020 | October | 16 | 16 | 2238 | 28500 | 7.853%
[29 empty] | 2020 | October | 16 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 16 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 16 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 16 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 16 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 16 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 16 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 17 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 17 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 17 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 17 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 17 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 17 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 17 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 17 | 7 | 599 | 28500 | 2.102%
[29 empty] | 2020 | October | 17 | 8 | 2276 | 28500 | 7.986%
[29 empty] | 2020 | October | 17 | 9 | 6092.5 | 28500 | 21.38%
[29 empty] | 2020 | October | 17 | 10 | 3845 | 28500 | 13.49%
[29 empty] | 2020 | October | 17 | 11 | 5538.5 | 28500 | 19.43%
[29 empty] | 2020 | October | 17 | 12 | 5106.5 | 28500 | 17.92%
[29 empty] | 2020 | October | 17 | 13 | 6835 | 28500 | 23.98%
[29 empty] | 2020 | October | 17 | 14 | 2962.5 | 28500 | 10.39%
[29 empty] | 2020 | October | 17 | 15 | 1843.5 | 28500 | 6.468%
[29 empty] | 2020 | October | 17 | 16 | 600 | 28500 | 2.105%
[29 empty] | 2020 | October | 17 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 17 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 17 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 17 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 17 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 17 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 17 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 18 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 18 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 18 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 18 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 18 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 18 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 18 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 18 | 7 | 2363 | 28500 | 8.291%
[29 empty] | 2020 | October | 18 | 8 | 5854.5 | 28500 | 20.54%
[29 empty] | 2020 | October | 18 | 9 | 4926.5 | 28500 | 17.29%
[29 empty] | 2020 | October | 18 | 10 | 9165 | 28500 | 32.16%
[29 empty] | 2020 | October | 18 | 11 | 9939.5 | 28500 | 34.88%
[29 empty] | 2020 | October | 18 | 12 | 8103 | 28500 | 28.43%
[29 empty] | 2020 | October | 18 | 13 | 9458.5 | 28500 | 33.19%
[29 empty] | 2020 | October | 18 | 14 | 3184 | 28500 | 11.17%
[29 empty] | 2020 | October | 18 | 15 | 4831.5 | 28500 | 16.95%
[29 empty] | 2020 | October | 18 | 16 | 782 | 28500 | 2.744%
[29 empty] | 2020 | October | 18 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 18 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 18 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 18 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 18 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 18 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 18 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 19 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 19 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 19 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 19 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 19 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 19 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 19 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 19 | 7 | 2306 | 28500 | 8.091%
[29 empty] | 2020 | October | 19 | 8 | 9905 | 28500 | 34.75%
[29 empty] | 2020 | October | 19 | 9 | 7788.5 | 28500 | 27.33%
[29 empty] | 2020 | October | 19 | 10 | 14644 | 28500 | 51.38%
[29 empty] | 2020 | October | 19 | 11 | 29351.5 | 28500 | 103%
[29 empty] | 2020 | October | 19 | 12 | 30083.5 | 28500 | 105.6%
[29 empty] | 2020 | October | 19 | 13 | 25804 | 28500 | 90.54%
[29 empty] | 2020 | October | 19 | 14 | 18902 | 28500 | 66.32%
[29 empty] | 2020 | October | 19 | 15 | 6256.5 | 28500 | 21.95%
[29 empty] | 2020 | October | 19 | 16 | 93 | 28500 | 0.3263%
[29 empty] | 2020 | October | 19 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 19 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 19 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 19 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 19 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 19 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 19 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 20 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 20 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 20 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 20 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 20 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 20 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 20 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 20 | 7 | 353 | 28500 | 1.239%
[29 empty] | 2020 | October | 20 | 8 | 4728.5 | 28500 | 16.59%
[29 empty] | 2020 | October | 20 | 9 | 620 | 28500 | 2.175%
[29 empty] | 2020 | October | 20 | 10 | 6918.5 | 28500 | 24.28%
[29 empty] | 2020 | October | 20 | 11 | 12924.5 | 28500 | 45.35%
[29 empty] | 2020 | October | 20 | 12 | 13185 | 28500 | 46.26%
[29 empty] | 2020 | October | 20 | 13 | 8325.5 | 28500 | 29.21%
[29 empty] | 2020 | October | 20 | 14 | 7196.5 | 28500 | 25.25%
[29 empty] | 2020 | October | 20 | 15 | 7680 | 28500 | 26.95%
[29 empty] | 2020 | October | 20 | 16 | 3115 | 28500 | 10.93%
[29 empty] | 2020 | October | 20 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 20 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 20 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 20 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 20 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 20 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 20 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 21 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 21 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 21 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 21 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 21 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 21 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 21 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 21 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 21 | 8 | 441 | 28500 | 1.547%
[29 empty] | 2020 | October | 21 | 9 | 500.5 | 28500 | 1.756%
[29 empty] | 2020 | October | 21 | 10 | 4033 | 28500 | 14.15%
[29 empty] | 2020 | October | 21 | 11 | 1711 | 28500 | 6.004%
[29 empty] | 2020 | October | 21 | 12 | 1713 | 28500 | 6.011%
[29 empty] | 2020 | October | 21 | 13 | 1427 | 28500 | 5.007%
[29 empty] | 2020 | October | 21 | 14 | 2558 | 28500 | 8.975%
[29 empty] | 2020 | October | 21 | 15 | 3124 | 28500 | 10.96%
[29 empty] | 2020 | October | 21 | 16 | 823 | 28500 | 2.888%
[29 empty] | 2020 | October | 21 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 21 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 21 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 21 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 21 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 21 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 21 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 22 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 22 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 22 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 22 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 22 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 22 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 22 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 22 | 7 | 2453 | 28500 | 8.607%
[29 empty] | 2020 | October | 22 | 8 | 5998 | 28500 | 21.05%
[29 empty] | 2020 | October | 22 | 9 | 5445 | 28500 | 19.11%
[29 empty] | 2020 | October | 22 | 10 | 26804.5 | 28500 | 94.05%
[29 empty] | 2020 | October | 22 | 11 | 911.5 | 28500 | 3.198%
[29 empty] | 2020 | October | 22 | 12 | 32813 | 28500 | 115.1%
[29 empty] | 2020 | October | 22 | 13 | 21435.5 | 28500 | 75.21%
[29 empty] | 2020 | October | 22 | 14 | 15235 | 28500 | 53.46%
[29 empty] | 2020 | October | 22 | 15 | 11480 | 28500 | 40.28%
[29 empty] | 2020 | October | 22 | 16 | 3984.5 | 28500 | 13.98%
[29 empty] | 2020 | October | 22 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 22 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 22 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 22 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 22 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 22 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 22 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 23 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 23 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 23 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 23 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 23 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 23 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 23 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 23 | 7 | 1416 | 28500 | 4.968%
[29 empty] | 2020 | October | 23 | 8 | 13778.5 | 28500 | 48.35%
[29 empty] | 2020 | October | 23 | 9 | 19678 | 28500 | 69.05%
[29 empty] | 2020 | October | 23 | 10 | 17116 | 28500 | 60.06%
[29 empty] | 2020 | October | 23 | 11 | 1150 | 28500 | 4.035%
[29 empty] | 2020 | October | 23 | 12 | 4153 | 28500 | 14.57%
[29 empty] | 2020 | October | 23 | 13 | 15785 | 28500 | 55.39%
[29 empty] | 2020 | October | 23 | 14 | 12006 | 28500 | 42.13%
[29 empty] | 2020 | October | 23 | 15 | 1082 | 28500 | 3.796%
[29 empty] | 2020 | October | 23 | 16 | 1890 | 28500 | 6.632%
[29 empty] | 2020 | October | 23 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 23 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 23 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 23 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 23 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 23 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 23 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 24 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 24 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 24 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 24 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 24 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 24 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 24 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 24 | 7 | 570 | 28500 | 2%
[29 empty] | 2020 | October | 24 | 8 | 3198.5 | 28500 | 11.22%
[29 empty] | 2020 | October | 24 | 9 | 4138.5 | 28500 | 14.52%
[29 empty] | 2020 | October | 24 | 10 | 6308.5 | 28500 | 22.14%
[29 empty] | 2020 | October | 24 | 11 | 10352 | 28500 | 36.32%
[29 empty] | 2020 | October | 24 | 12 | 4720 | 28500 | 16.56%
[29 empty] | 2020 | October | 24 | 13 | 8363.5 | 28500 | 29.35%
[29 empty] | 2020 | October | 24 | 14 | 6308.5 | 28500 | 22.14%
[29 empty] | 2020 | October | 24 | 15 | 1822 | 28500 | 6.393%
[29 empty] | 2020 | October | 24 | 16 | 515.5 | 28500 | 1.809%
[29 empty] | 2020 | October | 24 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 24 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 24 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 24 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 24 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 24 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 24 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 25 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 25 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 25 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 25 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 25 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 25 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 25 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 25 | 7 | 1811 | 28500 | 6.354%
[29 empty] | 2020 | October | 25 | 8 | 194 | 28500 | 0.6807%
[29 empty] | 2020 | October | 25 | 9 | 25509 | 28500 | 89.51%
[29 empty] | 2020 | October | 25 | 10 | 730.5 | 28500 | 2.563%
[29 empty] | 2020 | October | 25 | 11 | 4838 | 28500 | 16.98%
[29 empty] | 2020 | October | 25 | 12 | 35920 | 28500 | 126%
[29 empty] | 2020 | October | 25 | 13 | 6498.5 | 28500 | 22.8%
[29 empty] | 2020 | October | 25 | 14 | 26662.5 | 28500 | 93.55%
[29 empty] | 2020 | October | 25 | 15 | 15271.5 | 28500 | 53.58%
[29 empty] | 2020 | October | 25 | 16 | 4059 | 28500 | 14.24%
[29 empty] | 2020 | October | 25 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 25 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 25 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 25 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 25 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 25 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 25 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 26 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 26 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 26 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 26 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 26 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 26 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 26 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 26 | 7 | 1434.5 | 28500 | 5.033%
[29 empty] | 2020 | October | 26 | 8 | 14179 | 28500 | 49.75%
[29 empty] | 2020 | October | 26 | 9 | 23163 | 28500 | 81.27%
[29 empty] | 2020 | October | 26 | 10 | 27249 | 28500 | 95.61%
[29 empty] | 2020 | October | 26 | 11 | 10661.5 | 28500 | 37.41%
[29 empty] | 2020 | October | 26 | 12 | 25336 | 28500 | 88.9%
[29 empty] | 2020 | October | 26 | 13 | 6135.5 | 28500 | 21.53%
[29 empty] | 2020 | October | 26 | 14 | 4961.5 | 28500 | 17.41%
[29 empty] | 2020 | October | 26 | 15 | 4382 | 28500 | 15.38%
[29 empty] | 2020 | October | 26 | 16 | 1676 | 28500 | 5.881%
[29 empty] | 2020 | October | 26 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 26 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 26 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 26 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 26 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 26 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 26 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 27 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 27 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 27 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 27 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 27 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 27 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 27 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 27 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 27 | 8 | 873.5 | 28500 | 3.065%
[29 empty] | 2020 | October | 27 | 9 | 1573 | 28500 | 5.519%
[29 empty] | 2020 | October | 27 | 10 | 5258.5 | 28500 | 18.45%
[29 empty] | 2020 | October | 27 | 11 | 3298.5 | 28500 | 11.57%
[29 empty] | 2020 | October | 27 | 12 | 2186.5 | 28500 | 7.672%
[29 empty] | 2020 | October | 27 | 13 | 10896.5 | 28500 | 38.23%
[29 empty] | 2020 | October | 27 | 14 | 2899 | 28500 | 10.17%
[29 empty] | 2020 | October | 27 | 15 | 1265.5 | 28500 | 4.44%
[29 empty] | 2020 | October | 27 | 16 | 164.5 | 28500 | 0.5772%
[29 empty] | 2020 | October | 27 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 27 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 27 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 27 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 27 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 27 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 27 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 28 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 28 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 28 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 28 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 28 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 28 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 28 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 28 | 7 | 521.5 | 28500 | 1.83%
[29 empty] | 2020 | October | 28 | 8 | 12872.5 | 28500 | 45.17%
[29 empty] | 2020 | October | 28 | 9 | 4519 | 28500 | 15.86%
[29 empty] | 2020 | October | 28 | 10 | 12499 | 28500 | 43.86%
[29 empty] | 2020 | October | 28 | 11 | 13744.5 | 28500 | 48.23%
[29 empty] | 2020 | October | 28 | 12 | 28414 | 28500 | 99.7%
[29 empty] | 2020 | October | 28 | 13 | 6563.5 | 28500 | 23.03%
[29 empty] | 2020 | October | 28 | 14 | 6452.5 | 28500 | 22.64%
[29 empty] | 2020 | October | 28 | 15 | 14997.5 | 28500 | 52.62%
[29 empty] | 2020 | October | 28 | 16 | 325 | 28500 | 1.14%
[29 empty] | 2020 | October | 28 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 28 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 28 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 28 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 28 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 28 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 28 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 29 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 29 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 29 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 29 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 29 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 29 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 29 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 29 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 29 | 8 | 2138.5 | 28500 | 7.504%
[29 empty] | 2020 | October | 29 | 9 | 4081.5 | 28500 | 14.32%
[29 empty] | 2020 | October | 29 | 10 | 7268.5 | 28500 | 25.5%
[29 empty] | 2020 | October | 29 | 11 | 2219.5 | 28500 | 7.788%
[29 empty] | 2020 | October | 29 | 12 | 3394.5 | 28500 | 11.91%
[29 empty] | 2020 | October | 29 | 13 | 4470 | 28500 | 15.68%
[29 empty] | 2020 | October | 29 | 14 | 3946 | 28500 | 13.85%
[29 empty] | 2020 | October | 29 | 15 | 918 | 28500 | 3.221%
[29 empty] | 2020 | October | 29 | 16 | 12 | 28500 | 0.04211%
[29 empty] | 2020 | October | 29 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 29 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 29 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 29 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 29 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 29 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 29 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 30 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 30 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 30 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 30 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 30 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 30 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 30 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 30 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 30 | 8 | 3035 | 28500 | 10.65%
[29 empty] | 2020 | October | 30 | 9 | 1640.5 | 28500 | 5.756%
[29 empty] | 2020 | October | 30 | 10 | 2148 | 28500 | 7.537%
[29 empty] | 2020 | October | 30 | 11 | 1496 | 28500 | 5.249%
[29 empty] | 2020 | October | 30 | 12 | 3306 | 28500 | 11.6%
[29 empty] | 2020 | October | 30 | 13 | 2440.5 | 28500 | 8.563%
[29 empty] | 2020 | October | 30 | 14 | 2181.5 | 28500 | 7.654%
[29 empty] | 2020 | October | 30 | 15 | 2637.5 | 28500 | 9.254%
[29 empty] | 2020 | October | 30 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 30 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 30 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 30 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 30 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 30 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 30 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 30 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 31 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 31 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 31 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 31 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 31 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 31 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 31 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 31 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 31 | 8 | 214.5 | 28500 | 0.7526%
[29 empty] | 2020 | October | 31 | 9 | 14854.5 | 28500 | 52.12%
[29 empty] | 2020 | October | 31 | 10 | 21609.5 | 28500 | 75.82%
[29 empty] | 2020 | October | 31 | 11 | 713.5 | 28500 | 2.504%
[29 empty] | 2020 | October | 31 | 12 | 1457.5 | 28500 | 5.114%
[29 empty] | 2020 | October | 31 | 13 | 1608 | 28500 | 5.642%
[29 empty] | 2020 | October | 31 | 14 | 880.5 | 28500 | 3.089%
[29 empty] | 2020 | October | 31 | 15 | 2741.5 | 28500 | 9.619%
[29 empty] | 2020 | October | 31 | 16 | 530 | 28500 | 1.86%
[29 empty] | 2020 | October | 31 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 31 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 31 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 31 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 31 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 31 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | October | 31 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 1 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 1 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 1 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 1 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 1 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 1 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 1 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 1 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 1 | 8 | 1915 | 28500 | 6.719%
[29 empty] | 2020 | November | 1 | 9 | 7619 | 28500 | 26.73%
[29 empty] | 2020 | November | 1 | 10 | 13920.5 | 28500 | 48.84%
[29 empty] | 2020 | November | 1 | 11 | 6475.5 | 28500 | 22.72%
[29 empty] | 2020 | November | 1 | 12 | 6281 | 28500 | 22.04%
[29 empty] | 2020 | November | 1 | 13 | 3953.5 | 28500 | 13.87%
[29 empty] | 2020 | November | 1 | 14 | 4154.5 | 28500 | 14.58%
[29 empty] | 2020 | November | 1 | 15 | 1781 | 28500 | 6.249%
[29 empty] | 2020 | November | 1 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 1 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 1 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 1 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 1 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 1 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 1 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 1 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 2 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 2 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 2 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 2 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 2 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 2 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 2 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 2 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 2 | 8 | 2437.5 | 28500 | 8.553%
[29 empty] | 2020 | November | 2 | 9 | 3867 | 28500 | 13.57%
[29 empty] | 2020 | November | 2 | 10 | 2071.5 | 28500 | 7.268%
[29 empty] | 2020 | November | 2 | 11 | 17526 | 28500 | 61.49%
[29 empty] | 2020 | November | 2 | 12 | 28746 | 28500 | 100.9%
[29 empty] | 2020 | November | 2 | 13 | 30181 | 28500 | 105.9%
[29 empty] | 2020 | November | 2 | 14 | 14815.5 | 28500 | 51.98%
[29 empty] | 2020 | November | 2 | 15 | 14881 | 28500 | 52.21%
[29 empty] | 2020 | November | 2 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 2 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 2 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 2 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 2 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 2 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 2 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 2 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 3 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 3 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 3 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 3 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 3 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 3 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 3 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 3 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 3 | 8 | 9409.5 | 28500 | 33.02%
[29 empty] | 2020 | November | 3 | 9 | 2298 | 28500 | 8.063%
[29 empty] | 2020 | November | 3 | 10 | 25272.5 | 28500 | 88.68%
[29 empty] | 2020 | November | 3 | 11 | 17939.5 | 28500 | 62.95%
[29 empty] | 2020 | November | 3 | 12 | 12278.5 | 28500 | 43.08%
[29 empty] | 2020 | November | 3 | 13 | 6166 | 28500 | 21.64%
[29 empty] | 2020 | November | 3 | 14 | 8197 | 28500 | 28.76%
[29 empty] | 2020 | November | 3 | 15 | 10158.5 | 28500 | 35.64%
[29 empty] | 2020 | November | 3 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 3 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 3 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 3 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 3 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 3 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 3 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 3 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 4 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 4 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 4 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 4 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 4 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 4 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 4 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 4 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 4 | 8 | 13321 | 28500 | 46.74%
[29 empty] | 2020 | November | 4 | 9 | 23054.5 | 28500 | 80.89%
[29 empty] | 2020 | November | 4 | 10 | 29964.5 | 28500 | 105.1%
[29 empty] | 2020 | November | 4 | 11 | 32752.5 | 28500 | 114.9%
[29 empty] | 2020 | November | 4 | 12 | 34133 | 28500 | 119.8%
[29 empty] | 2020 | November | 4 | 13 | 32741 | 28500 | 114.9%
[29 empty] | 2020 | November | 4 | 14 | 23541 | 28500 | 82.6%
[29 empty] | 2020 | November | 4 | 15 | 15656.5 | 28500 | 54.94%
[29 empty] | 2020 | November | 4 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 4 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 4 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 4 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 4 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 4 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 4 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 4 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 5 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 5 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 5 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 5 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 5 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 5 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 5 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 5 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 5 | 8 | 7478.5 | 28500 | 26.24%
[29 empty] | 2020 | November | 5 | 9 | 12585.5 | 28500 | 44.16%
[29 empty] | 2020 | November | 5 | 10 | 9257.5 | 28500 | 32.48%
[29 empty] | 2020 | November | 5 | 11 | 11601.5 | 28500 | 40.71%
[29 empty] | 2020 | November | 5 | 12 | 15451.5 | 28500 | 54.22%
[29 empty] | 2020 | November | 5 | 13 | 19831.5 | 28500 | 69.58%
[29 empty] | 2020 | November | 5 | 14 | 18452 | 28500 | 64.74%
[29 empty] | 2020 | November | 5 | 15 | 13907.5 | 28500 | 48.8%
[29 empty] | 2020 | November | 5 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 5 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 5 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 5 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 5 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 5 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 5 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 5 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 6 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 6 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 6 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 6 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 6 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 6 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 6 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 6 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 6 | 8 | 3694 | 28500 | 12.96%
[29 empty] | 2020 | November | 6 | 9 | 2521.5 | 28500 | 8.847%
[29 empty] | 2020 | November | 6 | 10 | 6946.5 | 28500 | 24.37%
[29 empty] | 2020 | November | 6 | 11 | 6873.5 | 28500 | 24.12%
[29 empty] | 2020 | November | 6 | 12 | 6975 | 28500 | 24.47%
[29 empty] | 2020 | November | 6 | 13 | 4163.5 | 28500 | 14.61%
[29 empty] | 2020 | November | 6 | 14 | 4769 | 28500 | 16.73%
[29 empty] | 2020 | November | 6 | 15 | 13777 | 28500 | 48.34%
[29 empty] | 2020 | November | 6 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 6 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 6 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 6 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 6 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 6 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 6 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 6 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 7 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 7 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 7 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 7 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 7 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 7 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 7 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 7 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 7 | 8 | 6300 | 28500 | 22.11%
[29 empty] | 2020 | November | 7 | 9 | 13513.5 | 28500 | 47.42%
[29 empty] | 2020 | November | 7 | 10 | 27763.5 | 28500 | 97.42%
[29 empty] | 2020 | November | 7 | 11 | 29891 | 28500 | 104.9%
[29 empty] | 2020 | November | 7 | 12 | 31937 | 28500 | 112.1%
[29 empty] | 2020 | November | 7 | 13 | 28570.5 | 28500 | 100.2%
[29 empty] | 2020 | November | 7 | 14 | 21434 | 28500 | 75.21%
[29 empty] | 2020 | November | 7 | 15 | 14186.5 | 28500 | 49.78%
[29 empty] | 2020 | November | 7 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 7 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 7 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 7 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 7 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 7 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 7 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 7 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 8 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 8 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 8 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 8 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 8 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 8 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 8 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 8 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 8 | 8 | 1937 | 28500 | 6.796%
[29 empty] | 2020 | November | 8 | 9 | 8451 | 28500 | 29.65%
[29 empty] | 2020 | November | 8 | 10 | 25712 | 28500 | 90.22%
[29 empty] | 2020 | November | 8 | 11 | 17213 | 28500 | 60.4%
[29 empty] | 2020 | November | 8 | 12 | 8529.5 | 28500 | 29.93%
[29 empty] | 2020 | November | 8 | 13 | 4451 | 28500 | 15.62%
[29 empty] | 2020 | November | 8 | 14 | 1351.5 | 28500 | 4.742%
[29 empty] | 2020 | November | 8 | 15 | 877.5 | 28500 | 3.079%
[29 empty] | 2020 | November | 8 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 8 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 8 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 8 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 8 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 8 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 8 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 8 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 9 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 9 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 9 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 9 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 9 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 9 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 9 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 9 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 9 | 8 | 2549 | 28500 | 8.944%
[29 empty] | 2020 | November | 9 | 9 | 2375 | 28500 | 8.333%
[29 empty] | 2020 | November | 9 | 10 | 1431.5 | 28500 | 5.023%
[29 empty] | 2020 | November | 9 | 11 | 19653.5 | 28500 | 68.96%
[29 empty] | 2020 | November | 9 | 12 | 12460 | 28500 | 43.72%
[29 empty] | 2020 | November | 9 | 13 | 13258.5 | 28500 | 46.52%
[29 empty] | 2020 | November | 9 | 14 | 16062.5 | 28500 | 56.36%
[29 empty] | 2020 | November | 9 | 15 | 11914 | 28500 | 41.8%
[29 empty] | 2020 | November | 9 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 9 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 9 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 9 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 9 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 9 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 9 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 9 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 10 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 10 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 10 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 10 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 10 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 10 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 10 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 10 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 10 | 8 | 1820.5 | 28500 | 6.388%
[29 empty] | 2020 | November | 10 | 9 | 14519.5 | 28500 | 50.95%
[29 empty] | 2020 | November | 10 | 10 | 19501.5 | 28500 | 68.43%
[29 empty] | 2020 | November | 10 | 11 | 29805 | 28500 | 104.6%
[29 empty] | 2020 | November | 10 | 12 | 10222 | 28500 | 35.87%
[29 empty] | 2020 | November | 10 | 13 | 2932.5 | 28500 | 10.29%
[29 empty] | 2020 | November | 10 | 14 | 3099 | 28500 | 10.87%
[29 empty] | 2020 | November | 10 | 15 | 4119.5 | 28500 | 14.45%
[29 empty] | 2020 | November | 10 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 10 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 10 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 10 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 10 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 10 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 10 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 10 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 11 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 11 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 11 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 11 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 11 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 11 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 11 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 11 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 11 | 8 | 698.5 | 28500 | 2.451%
[29 empty] | 2020 | November | 11 | 9 | 4482 | 28500 | 15.73%
[29 empty] | 2020 | November | 11 | 10 | 6945.5 | 28500 | 24.37%
[29 empty] | 2020 | November | 11 | 11 | 15206.5 | 28500 | 53.36%
[29 empty] | 2020 | November | 11 | 12 | 3763.5 | 28500 | 13.21%
[29 empty] | 2020 | November | 11 | 13 | 1401.5 | 28500 | 4.918%
[29 empty] | 2020 | November | 11 | 14 | 3314 | 28500 | 11.63%
[29 empty] | 2020 | November | 11 | 15 | 723.5 | 28500 | 2.539%
[29 empty] | 2020 | November | 11 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 11 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 11 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 11 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 11 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 11 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 11 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 11 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 12 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 12 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 12 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 12 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 12 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 12 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 12 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 12 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 12 | 8 | 8641 | 28500 | 30.32%
[29 empty] | 2020 | November | 12 | 9 | 19789 | 28500 | 69.44%
[29 empty] | 2020 | November | 12 | 10 | 27587 | 28500 | 96.8%
[29 empty] | 2020 | November | 12 | 11 | 21868 | 28500 | 76.73%
[29 empty] | 2020 | November | 12 | 12 | 22499.5 | 28500 | 78.95%
[29 empty] | 2020 | November | 12 | 13 | 27845.5 | 28500 | 97.7%
[29 empty] | 2020 | November | 12 | 14 | 20937.5 | 28500 | 73.46%
[29 empty] | 2020 | November | 12 | 15 | 1431.5 | 28500 | 5.023%
[29 empty] | 2020 | November | 12 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 12 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 12 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 12 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 12 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 12 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 12 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 12 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 13 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 13 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 13 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 13 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 13 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 13 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 13 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 13 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 13 | 8 | 629 | 28500 | 2.207%
[29 empty] | 2020 | November | 13 | 9 | 4485.5 | 28500 | 15.74%
[29 empty] | 2020 | November | 13 | 10 | 10009 | 28500 | 35.12%
[29 empty] | 2020 | November | 13 | 11 | 13586 | 28500 | 47.67%
[29 empty] | 2020 | November | 13 | 12 | 30880 | 28500 | 108.4%
[29 empty] | 2020 | November | 13 | 13 | 21396 | 28500 | 75.07%
[29 empty] | 2020 | November | 13 | 14 | 15965 | 28500 | 56.02%
[29 empty] | 2020 | November | 13 | 15 | 11029 | 28500 | 38.7%
[29 empty] | 2020 | November | 13 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 13 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 13 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 13 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 13 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 13 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 13 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 13 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 14 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 14 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 14 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 14 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 14 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 14 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 14 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 14 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 14 | 8 | 269 | 28500 | 0.9439%
[29 empty] | 2020 | November | 14 | 9 | 215 | 28500 | 0.7544%
[29 empty] | 2020 | November | 14 | 10 | 4517 | 28500 | 15.85%
[29 empty] | 2020 | November | 14 | 11 | 1538.5 | 28500 | 5.398%
[29 empty] | 2020 | November | 14 | 12 | 5142 | 28500 | 18.04%
[29 empty] | 2020 | November | 14 | 13 | 3126 | 28500 | 10.97%
[29 empty] | 2020 | November | 14 | 14 | 4469.5 | 28500 | 15.68%
[29 empty] | 2020 | November | 14 | 15 | 9509.5 | 28500 | 33.37%
[29 empty] | 2020 | November | 14 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 14 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 14 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 14 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 14 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 14 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 14 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 14 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 15 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 15 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 15 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 15 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 15 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 15 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 15 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 15 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 15 | 8 | 296.5 | 28500 | 1.04%
[29 empty] | 2020 | November | 15 | 9 | 4556.5 | 28500 | 15.99%
[29 empty] | 2020 | November | 15 | 10 | 2328 | 28500 | 8.168%
[29 empty] | 2020 | November | 15 | 11 | 7323 | 28500 | 25.69%
[29 empty] | 2020 | November | 15 | 12 | 32685.5 | 28500 | 114.7%
[29 empty] | 2020 | November | 15 | 13 | 29524 | 28500 | 103.6%
[29 empty] | 2020 | November | 15 | 14 | 21873.5 | 28500 | 76.75%
[29 empty] | 2020 | November | 15 | 15 | 274.5 | 28500 | 0.9632%
[29 empty] | 2020 | November | 15 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 15 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 15 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 15 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 15 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 15 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 15 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 15 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 16 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 16 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 16 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 16 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 16 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 16 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 16 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 16 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 16 | 8 | 31.5 | 28500 | 0.1105%
[29 empty] | 2020 | November | 16 | 9 | 1318 | 28500 | 4.625%
[29 empty] | 2020 | November | 16 | 10 | 1713 | 28500 | 6.011%
[29 empty] | 2020 | November | 16 | 11 | 1971 | 28500 | 6.916%
[29 empty] | 2020 | November | 16 | 12 | 14059.5 | 28500 | 49.33%
[29 empty] | 2020 | November | 16 | 13 | 11162.5 | 28500 | 39.17%
[29 empty] | 2020 | November | 16 | 14 | 2606 | 28500 | 9.144%
[29 empty] | 2020 | November | 16 | 15 | 3329 | 28500 | 11.68%
[29 empty] | 2020 | November | 16 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 16 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 16 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 16 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 16 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 16 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 16 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 16 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 17 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 17 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 17 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 17 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 17 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 17 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 17 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 17 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 17 | 8 | 982.5 | 28500 | 3.447%
[29 empty] | 2020 | November | 17 | 9 | 5034 | 28500 | 17.66%
[29 empty] | 2020 | November | 17 | 10 | 6946.5 | 28500 | 24.37%
[29 empty] | 2020 | November | 17 | 11 | 2837 | 28500 | 9.954%
[29 empty] | 2020 | November | 17 | 12 | 3019.5 | 28500 | 10.59%
[29 empty] | 2020 | November | 17 | 13 | 7767.5 | 28500 | 27.25%
[29 empty] | 2020 | November | 17 | 14 | 561 | 28500 | 1.968%
[29 empty] | 2020 | November | 17 | 15 | 1224.5 | 28500 | 4.296%
[29 empty] | 2020 | November | 17 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 17 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 17 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 17 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 17 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 17 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 17 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 17 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 18 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 18 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 18 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 18 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 18 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 18 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 18 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 18 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 18 | 8 | 4239.5 | 28500 | 14.88%
[29 empty] | 2020 | November | 18 | 9 | 15328 | 28500 | 53.78%
[29 empty] | 2020 | November | 18 | 10 | 21014.5 | 28500 | 73.74%
[29 empty] | 2020 | November | 18 | 11 | 16912.5 | 28500 | 59.34%
[29 empty] | 2020 | November | 18 | 12 | 28876.5 | 28500 | 101.3%
[29 empty] | 2020 | November | 18 | 13 | 4111.5 | 28500 | 14.43%
[29 empty] | 2020 | November | 18 | 14 | 409.5 | 28500 | 1.437%
[29 empty] | 2020 | November | 18 | 15 | 499 | 28500 | 1.751%
[29 empty] | 2020 | November | 18 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 18 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 18 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 18 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 18 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 18 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 18 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 18 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 19 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 19 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 19 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 19 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 19 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 19 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 19 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 19 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 19 | 8 | 736.5 | 28500 | 2.584%
[29 empty] | 2020 | November | 19 | 9 | 3779 | 28500 | 13.26%
[29 empty] | 2020 | November | 19 | 10 | 5062 | 28500 | 17.76%
[29 empty] | 2020 | November | 19 | 11 | 1290 | 28500 | 4.526%
[29 empty] | 2020 | November | 19 | 12 | 2594 | 28500 | 9.102%
[29 empty] | 2020 | November | 19 | 13 | 1047 | 28500 | 3.674%
[29 empty] | 2020 | November | 19 | 14 | 17148.5 | 28500 | 60.17%
[29 empty] | 2020 | November | 19 | 15 | 10208.5 | 28500 | 35.82%
[29 empty] | 2020 | November | 19 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 19 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 19 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 19 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 19 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 19 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 19 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 19 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 20 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 20 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 20 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 20 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 20 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 20 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 20 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 20 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 20 | 8 | 976.5 | 28500 | 3.426%
[29 empty] | 2020 | November | 20 | 9 | 5724.5 | 28500 | 20.09%
[29 empty] | 2020 | November | 20 | 10 | 19946.5 | 28500 | 69.99%
[29 empty] | 2020 | November | 20 | 11 | 8389.5 | 28500 | 29.44%
[29 empty] | 2020 | November | 20 | 12 | 6912.5 | 28500 | 24.25%
[29 empty] | 2020 | November | 20 | 13 | 7138 | 28500 | 25.05%
[29 empty] | 2020 | November | 20 | 14 | 6358.5 | 28500 | 22.31%
[29 empty] | 2020 | November | 20 | 15 | 1455 | 28500 | 5.105%
[29 empty] | 2020 | November | 20 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 20 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 20 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 20 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 20 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 20 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 20 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 20 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 21 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 21 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 21 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 21 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 21 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 21 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 21 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 21 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 21 | 8 | 4163 | 28500 | 14.61%
[29 empty] | 2020 | November | 21 | 9 | 1139.5 | 28500 | 3.998%
[29 empty] | 2020 | November | 21 | 10 | 4970 | 28500 | 17.44%
[29 empty] | 2020 | November | 21 | 11 | 6442 | 28500 | 22.6%
[29 empty] | 2020 | November | 21 | 12 | 1882.5 | 28500 | 6.605%
[29 empty] | 2020 | November | 21 | 13 | 4847.5 | 28500 | 17.01%
[29 empty] | 2020 | November | 21 | 14 | 1627 | 28500 | 5.709%
[29 empty] | 2020 | November | 21 | 15 | 3964 | 28500 | 13.91%
[29 empty] | 2020 | November | 21 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 21 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 21 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 21 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 21 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 21 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 21 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 21 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 22 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 22 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 22 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 22 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 22 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 22 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 22 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 22 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 22 | 8 | 1208.5 | 28500 | 4.24%
[29 empty] | 2020 | November | 22 | 9 | 4740 | 28500 | 16.63%
[29 empty] | 2020 | November | 22 | 10 | 7981.5 | 28500 | 28.01%
[29 empty] | 2020 | November | 22 | 11 | 30002.5 | 28500 | 105.3%
[29 empty] | 2020 | November | 22 | 12 | 5192.5 | 28500 | 18.22%
[29 empty] | 2020 | November | 22 | 13 | 20529 | 28500 | 72.03%
[29 empty] | 2020 | November | 22 | 14 | 17929 | 28500 | 62.91%
[29 empty] | 2020 | November | 22 | 15 | 8425 | 28500 | 29.56%
[29 empty] | 2020 | November | 22 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 22 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 22 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 22 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 22 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 22 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 22 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 22 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 23 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 23 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 23 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 23 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 23 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 23 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 23 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 23 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 23 | 8 | 929 | 28500 | 3.26%
[29 empty] | 2020 | November | 23 | 9 | 18113.5 | 28500 | 63.56%
[29 empty] | 2020 | November | 23 | 10 | 25769 | 28500 | 90.42%
[29 empty] | 2020 | November | 23 | 11 | 18897 | 28500 | 66.31%
[29 empty] | 2020 | November | 23 | 12 | 5458 | 28500 | 19.15%
[29 empty] | 2020 | November | 23 | 13 | 2579.5 | 28500 | 9.051%
[29 empty] | 2020 | November | 23 | 14 | 4730.5 | 28500 | 16.6%
[29 empty] | 2020 | November | 23 | 15 | 5844 | 28500 | 20.51%
[29 empty] | 2020 | November | 23 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 23 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 23 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 23 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 23 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 23 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 23 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 23 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 24 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 24 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 24 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 24 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 24 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 24 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 24 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 24 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 24 | 8 | 248 | 28500 | 0.8702%
[29 empty] | 2020 | November | 24 | 9 | 3810 | 28500 | 13.37%
[29 empty] | 2020 | November | 24 | 10 | 26942.5 | 28500 | 94.54%
[29 empty] | 2020 | November | 24 | 11 | 10351.5 | 28500 | 36.32%
[29 empty] | 2020 | November | 24 | 12 | 22484.5 | 28500 | 78.89%
[29 empty] | 2020 | November | 24 | 13 | 24147 | 28500 | 84.73%
[29 empty] | 2020 | November | 24 | 14 | 5491 | 28500 | 19.27%
[29 empty] | 2020 | November | 24 | 15 | 4214.5 | 28500 | 14.79%
[29 empty] | 2020 | November | 24 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 24 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 24 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 24 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 24 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 24 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 24 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 24 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 25 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 25 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 25 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 25 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 25 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 25 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 25 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 25 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 25 | 8 | 219.5 | 28500 | 0.7702%
[29 empty] | 2020 | November | 25 | 9 | 245.5 | 28500 | 0.8614%
[29 empty] | 2020 | November | 25 | 10 | 826.5 | 28500 | 2.9%
[29 empty] | 2020 | November | 25 | 11 | 443.5 | 28500 | 1.556%
[29 empty] | 2020 | November | 25 | 12 | 2095.5 | 28500 | 7.353%
[29 empty] | 2020 | November | 25 | 13 | 2133.5 | 28500 | 7.486%
[29 empty] | 2020 | November | 25 | 14 | 856 | 28500 | 3.004%
[29 empty] | 2020 | November | 25 | 15 | 217 | 28500 | 0.7614%
[29 empty] | 2020 | November | 25 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 25 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 25 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 25 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 25 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 25 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 25 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 25 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 26 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 26 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 26 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 26 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 26 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 26 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 26 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 26 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 26 | 8 | 76.5 | 28500 | 0.2684%
[29 empty] | 2020 | November | 26 | 9 | 890 | 28500 | 3.123%
[29 empty] | 2020 | November | 26 | 10 | 3256 | 28500 | 11.42%
[29 empty] | 2020 | November | 26 | 11 | 2040 | 28500 | 7.158%
[29 empty] | 2020 | November | 26 | 12 | 878 | 28500 | 3.081%
[29 empty] | 2020 | November | 26 | 13 | 1330 | 28500 | 4.667%
[29 empty] | 2020 | November | 26 | 14 | 423.5 | 28500 | 1.486%
[29 empty] | 2020 | November | 26 | 15 | 335 | 28500 | 1.175%
[29 empty] | 2020 | November | 26 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 26 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 26 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 26 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 26 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 26 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 26 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 26 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 27 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 27 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 27 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 27 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 27 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 27 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 27 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 27 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 27 | 8 | 894 | 28500 | 3.137%
[29 empty] | 2020 | November | 27 | 9 | 2844 | 28500 | 9.979%
[29 empty] | 2020 | November | 27 | 10 | 13370.5 | 28500 | 46.91%
[29 empty] | 2020 | November | 27 | 11 | 8501.5 | 28500 | 29.83%
[29 empty] | 2020 | November | 27 | 12 | 13636.5 | 28500 | 47.85%
[29 empty] | 2020 | November | 27 | 13 | 20595 | 28500 | 72.26%
[29 empty] | 2020 | November | 27 | 14 | 4027 | 28500 | 14.13%
[29 empty] | 2020 | November | 27 | 15 | 2036.5 | 28500 | 7.146%
[29 empty] | 2020 | November | 27 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 27 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 27 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 27 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 27 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 27 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 27 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 27 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 28 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 28 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 28 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 28 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 28 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 28 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 28 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 28 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 28 | 8 | 14.5 | 28500 | 0.05088%
[29 empty] | 2020 | November | 28 | 9 | 1411 | 28500 | 4.951%
[29 empty] | 2020 | November | 28 | 10 | 1882 | 28500 | 6.604%
[29 empty] | 2020 | November | 28 | 11 | 2248.5 | 28500 | 7.889%
[29 empty] | 2020 | November | 28 | 12 | 3147 | 28500 | 11.04%
[29 empty] | 2020 | November | 28 | 13 | 4902 | 28500 | 17.2%
[29 empty] | 2020 | November | 28 | 14 | 5901 | 28500 | 20.71%
[29 empty] | 2020 | November | 28 | 15 | 6381.5 | 28500 | 22.39%
[29 empty] | 2020 | November | 28 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 28 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 28 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 28 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 28 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 28 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 28 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 28 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 29 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 29 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 29 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 29 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 29 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 29 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 29 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 29 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 29 | 8 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 29 | 9 | 679.5 | 28500 | 2.384%
[29 empty] | 2020 | November | 29 | 10 | 1553 | 28500 | 5.449%
[29 empty] | 2020 | November | 29 | 11 | 1919.5 | 28500 | 6.735%
[29 empty] | 2020 | November | 29 | 12 | 1916 | 28500 | 6.723%
[29 empty] | 2020 | November | 29 | 13 | 2251 | 28500 | 7.898%
[29 empty] | 2020 | November | 29 | 14 | 1150.5 | 28500 | 4.037%
[29 empty] | 2020 | November | 29 | 15 | 363.5 | 28500 | 1.275%
[29 empty] | 2020 | November | 29 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 29 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 29 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 29 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 29 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 29 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 29 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 29 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 30 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 30 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 30 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 30 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 30 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 30 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 30 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 30 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 30 | 8 | 813.5 | 28500 | 2.854%
[29 empty] | 2020 | November | 30 | 9 | 98.5 | 28500 | 0.3456%
[29 empty] | 2020 | November | 30 | 10 | 585 | 28500 | 2.053%
[29 empty] | 2020 | November | 30 | 11 | 1820 | 28500 | 6.386%
[29 empty] | 2020 | November | 30 | 12 | 3039.5 | 28500 | 10.66%
[29 empty] | 2020 | November | 30 | 13 | 712 | 28500 | 2.498%
[29 empty] | 2020 | November | 30 | 14 | 2024.5 | 28500 | 7.104%
[29 empty] | 2020 | November | 30 | 15 | 2253 | 28500 | 7.905%
[29 empty] | 2020 | November | 30 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 30 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 30 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 30 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 30 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 30 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 30 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | November | 30 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 1 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 1 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 1 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 1 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 1 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 1 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 1 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 1 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 1 | 8 | 77 | 28500 | 0.2702%
[29 empty] | 2020 | December | 1 | 9 | 14708 | 28500 | 51.61%
[29 empty] | 2020 | December | 1 | 10 | 24213.5 | 28500 | 84.96%
[29 empty] | 2020 | December | 1 | 11 | 24997.5 | 28500 | 87.71%
[29 empty] | 2020 | December | 1 | 12 | 28530 | 28500 | 100.1%
[29 empty] | 2020 | December | 1 | 13 | 27007 | 28500 | 94.76%
[29 empty] | 2020 | December | 1 | 14 | 5639.5 | 28500 | 19.79%
[29 empty] | 2020 | December | 1 | 15 | 4298 | 28500 | 15.08%
[29 empty] | 2020 | December | 1 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 1 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 1 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 1 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 1 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 1 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 1 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 1 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 2 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 2 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 2 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 2 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 2 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 2 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 2 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 2 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 2 | 8 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 2 | 9 | 407 | 28500 | 1.428%
[29 empty] | 2020 | December | 2 | 10 | 897.5 | 28500 | 3.149%
[29 empty] | 2020 | December | 2 | 11 | 4571.5 | 28500 | 16.04%
[29 empty] | 2020 | December | 2 | 12 | 11403.5 | 28500 | 40.01%
[29 empty] | 2020 | December | 2 | 13 | 7194.5 | 28500 | 25.24%
[29 empty] | 2020 | December | 2 | 14 | 3003 | 28500 | 10.54%
[29 empty] | 2020 | December | 2 | 15 | 54 | 28500 | 0.1895%
[29 empty] | 2020 | December | 2 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 2 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 2 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 2 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 2 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 2 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 2 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 2 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 3 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 3 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 3 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 3 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 3 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 3 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 3 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 3 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 3 | 8 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 3 | 9 | 754.5 | 28500 | 2.647%
[29 empty] | 2020 | December | 3 | 10 | 1866.5 | 28500 | 6.549%
[29 empty] | 2020 | December | 3 | 11 | 1562.5 | 28500 | 5.482%
[29 empty] | 2020 | December | 3 | 12 | 1377 | 28500 | 4.832%
[29 empty] | 2020 | December | 3 | 13 | 583.5 | 28500 | 2.047%
[29 empty] | 2020 | December | 3 | 14 | 252 | 28500 | 0.8842%
[29 empty] | 2020 | December | 3 | 15 | 53.5 | 28500 | 0.1877%
[29 empty] | 2020 | December | 3 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 3 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 3 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 3 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 3 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 3 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 3 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 3 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 4 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 4 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 4 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 4 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 4 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 4 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 4 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 4 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 4 | 8 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 4 | 9 | 258.5 | 28500 | 0.907%
[29 empty] | 2020 | December | 4 | 10 | 1006 | 28500 | 3.53%
[29 empty] | 2020 | December | 4 | 11 | 628 | 28500 | 2.204%
[29 empty] | 2020 | December | 4 | 12 | 5192.5 | 28500 | 18.22%
[29 empty] | 2020 | December | 4 | 13 | 5635 | 28500 | 19.77%
[29 empty] | 2020 | December | 4 | 14 | 9430 | 28500 | 33.09%
[29 empty] | 2020 | December | 4 | 15 | 2741.5 | 28500 | 9.619%
[29 empty] | 2020 | December | 4 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 4 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 4 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 4 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 4 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 4 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 4 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 4 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 5 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 5 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 5 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 5 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 5 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 5 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 5 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 5 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 5 | 8 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 5 | 9 | 16188.5 | 28500 | 56.8%
[29 empty] | 2020 | December | 5 | 10 | 25096.5 | 28500 | 88.06%
[29 empty] | 2020 | December | 5 | 11 | 22327 | 28500 | 78.34%
[29 empty] | 2020 | December | 5 | 12 | 20949 | 28500 | 73.51%
[29 empty] | 2020 | December | 5 | 13 | 6883 | 28500 | 24.15%
[29 empty] | 2020 | December | 5 | 14 | 4227 | 28500 | 14.83%
[29 empty] | 2020 | December | 5 | 15 | 674 | 28500 | 2.365%
[29 empty] | 2020 | December | 5 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 5 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 5 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 5 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 5 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 5 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 5 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 5 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 6 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 6 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 6 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 6 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 6 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 6 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 6 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 6 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 6 | 8 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 6 | 9 | 595.5 | 28500 | 2.089%
[29 empty] | 2020 | December | 6 | 10 | 3295 | 28500 | 11.56%
[29 empty] | 2020 | December | 6 | 11 | 2174 | 28500 | 7.628%
[29 empty] | 2020 | December | 6 | 12 | 4395 | 28500 | 15.42%
[29 empty] | 2020 | December | 6 | 13 | 6423.5 | 28500 | 22.54%
[29 empty] | 2020 | December | 6 | 14 | 1092.5 | 28500 | 3.833%
[29 empty] | 2020 | December | 6 | 15 | 3446 | 28500 | 12.09%
[29 empty] | 2020 | December | 6 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 6 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 6 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 6 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 6 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 6 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 6 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 6 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 7 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 7 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 7 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 7 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 7 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 7 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 7 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 7 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 7 | 8 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 7 | 9 | 2856 | 28500 | 10.02%
[29 empty] | 2020 | December | 7 | 10 | 1597 | 28500 | 5.604%
[29 empty] | 2020 | December | 7 | 11 | 6606.5 | 28500 | 23.18%
[29 empty] | 2020 | December | 7 | 12 | 6663.5 | 28500 | 23.38%
[29 empty] | 2020 | December | 7 | 13 | 2268.5 | 28500 | 7.96%
[29 empty] | 2020 | December | 7 | 14 | 6649.5 | 28500 | 23.33%
[29 empty] | 2020 | December | 7 | 15 | 620.5 | 28500 | 2.177%
[29 empty] | 2020 | December | 7 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 7 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 7 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 7 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 7 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 7 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 7 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 7 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 8 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 8 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 8 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 8 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 8 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 8 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 8 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 8 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 8 | 8 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 8 | 9 | 1378.5 | 28500 | 4.837%
[29 empty] | 2020 | December | 8 | 10 | 2345.5 | 28500 | 8.23%
[29 empty] | 2020 | December | 8 | 11 | 13243.5 | 28500 | 46.47%
[29 empty] | 2020 | December | 8 | 12 | 20098 | 28500 | 70.52%
[29 empty] | 2020 | December | 8 | 13 | 24729.5 | 28500 | 86.77%
[29 empty] | 2020 | December | 8 | 14 | 18429.5 | 28500 | 64.66%
[29 empty] | 2020 | December | 8 | 15 | 4593.5 | 28500 | 16.12%
[29 empty] | 2020 | December | 8 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 8 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 8 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 8 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 8 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 8 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 8 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 8 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 9 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 9 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 9 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 9 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 9 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 9 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 9 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 9 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 9 | 8 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 9 | 9 | 12065.5 | 28500 | 42.34%
[29 empty] | 2020 | December | 9 | 10 | 4232.5 | 28500 | 14.85%
[29 empty] | 2020 | December | 9 | 11 | 14444 | 28500 | 50.68%
[29 empty] | 2020 | December | 9 | 12 | 11996.5 | 28500 | 42.09%
[29 empty] | 2020 | December | 9 | 13 | 10284.5 | 28500 | 36.09%
[29 empty] | 2020 | December | 9 | 14 | 3152.5 | 28500 | 11.06%
[29 empty] | 2020 | December | 9 | 15 | 1322.5 | 28500 | 4.64%
[29 empty] | 2020 | December | 9 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 9 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 9 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 9 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 9 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 9 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 9 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 9 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 10 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 10 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 10 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 10 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 10 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 10 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 10 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 10 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 10 | 8 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 10 | 9 | 491.5 | 28500 | 1.725%
[29 empty] | 2020 | December | 10 | 10 | 1023.5 | 28500 | 3.591%
[29 empty] | 2020 | December | 10 | 11 | 1559.5 | 28500 | 5.472%
[29 empty] | 2020 | December | 10 | 12 | 1741 | 28500 | 6.109%
[29 empty] | 2020 | December | 10 | 13 | 1927.5 | 28500 | 6.763%
[29 empty] | 2020 | December | 10 | 14 | 519 | 28500 | 1.821%
[29 empty] | 2020 | December | 10 | 15 | 519 | 28500 | 1.821%
[29 empty] | 2020 | December | 10 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 10 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 10 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 10 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 10 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 10 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 10 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 10 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 11 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 11 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 11 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 11 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 11 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 11 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 11 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 11 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 11 | 8 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 11 | 9 | 7933 | 28500 | 27.84%
[29 empty] | 2020 | December | 11 | 10 | 6172.5 | 28500 | 21.66%
[29 empty] | 2020 | December | 11 | 11 | 735 | 28500 | 2.579%
[29 empty] | 2020 | December | 11 | 12 | 1422 | 28500 | 4.989%
[29 empty] | 2020 | December | 11 | 13 | 5929.5 | 28500 | 20.81%
[29 empty] | 2020 | December | 11 | 14 | 2485.5 | 28500 | 8.721%
[29 empty] | 2020 | December | 11 | 15 | 5962.5 | 28500 | 20.92%
[29 empty] | 2020 | December | 11 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 11 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 11 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 11 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 11 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 11 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 11 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 11 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 12 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 12 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 12 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 12 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 12 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 12 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 12 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 12 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 12 | 8 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 12 | 9 | 1433 | 28500 | 5.028%
[29 empty] | 2020 | December | 12 | 10 | 2510 | 28500 | 8.807%
[29 empty] | 2020 | December | 12 | 11 | 2531 | 28500 | 8.881%
[29 empty] | 2020 | December | 12 | 12 | 2031.5 | 28500 | 7.128%
[29 empty] | 2020 | December | 12 | 13 | 1406 | 28500 | 4.933%
[29 empty] | 2020 | December | 12 | 14 | 120.5 | 28500 | 0.4228%
[29 empty] | 2020 | December | 12 | 15 | 97.5 | 28500 | 0.3421%
[29 empty] | 2020 | December | 12 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 12 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 12 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 12 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 12 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 12 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 12 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 12 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 13 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 13 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 13 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 13 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 13 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 13 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 13 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 13 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 13 | 8 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 13 | 9 | 2727.5 | 28500 | 9.57%
[29 empty] | 2020 | December | 13 | 10 | 1091 | 28500 | 3.828%
[29 empty] | 2020 | December | 13 | 11 | 1409 | 28500 | 4.944%
[29 empty] | 2020 | December | 13 | 12 | 549 | 28500 | 1.926%
[29 empty] | 2020 | December | 13 | 13 | 455 | 28500 | 1.596%
[29 empty] | 2020 | December | 13 | 14 | 610.5 | 28500 | 2.142%
[29 empty] | 2020 | December | 13 | 15 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 13 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 13 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 13 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 13 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 13 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 13 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 13 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 13 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 14 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 14 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 14 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 14 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 14 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 14 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 14 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 14 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 14 | 8 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 14 | 9 | 10752 | 28500 | 37.73%
[29 empty] | 2020 | December | 14 | 10 | 14211.5 | 28500 | 49.86%
[29 empty] | 2020 | December | 14 | 11 | 2040.5 | 28500 | 7.16%
[29 empty] | 2020 | December | 14 | 12 | 19807.5 | 28500 | 69.5%
[29 empty] | 2020 | December | 14 | 13 | 8004 | 28500 | 28.08%
[29 empty] | 2020 | December | 14 | 14 | 2827 | 28500 | 9.919%
[29 empty] | 2020 | December | 14 | 15 | 616.5 | 28500 | 2.163%
[29 empty] | 2020 | December | 14 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 14 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 14 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 14 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 14 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 14 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 14 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 14 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 15 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 15 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 15 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 15 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 15 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 15 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 15 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 15 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 15 | 8 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 15 | 9 | 8466 | 28500 | 29.71%
[29 empty] | 2020 | December | 15 | 10 | 21292.5 | 28500 | 74.71%
[29 empty] | 2020 | December | 15 | 11 | 28353.5 | 28500 | 99.49%
[29 empty] | 2020 | December | 15 | 12 | 3827 | 28500 | 13.43%
[29 empty] | 2020 | December | 15 | 13 | 274 | 28500 | 0.9614%
[29 empty] | 2020 | December | 15 | 14 | 18175.5 | 28500 | 63.77%
[29 empty] | 2020 | December | 15 | 15 | 2076 | 28500 | 7.284%
[29 empty] | 2020 | December | 15 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 15 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 15 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 15 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 15 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 15 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 15 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 15 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 16 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 16 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 16 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 16 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 16 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 16 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 16 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 16 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 16 | 8 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 16 | 9 | 13438.5 | 28500 | 47.15%
[29 empty] | 2020 | December | 16 | 10 | 17811 | 28500 | 62.49%
[29 empty] | 2020 | December | 16 | 11 | 25908 | 28500 | 90.91%
[29 empty] | 2020 | December | 16 | 12 | 6123 | 28500 | 21.48%
[29 empty] | 2020 | December | 16 | 13 | 2259.5 | 28500 | 7.928%
[29 empty] | 2020 | December | 16 | 14 | 3591 | 28500 | 12.6%
[29 empty] | 2020 | December | 16 | 15 | 586.5 | 28500 | 2.058%
[29 empty] | 2020 | December | 16 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 16 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 16 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 16 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 16 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 16 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 16 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 16 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 17 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 17 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 17 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 17 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 17 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 17 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 17 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 17 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 17 | 8 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 17 | 9 | 13405 | 28500 | 47.04%
[29 empty] | 2020 | December | 17 | 10 | 22968 | 28500 | 80.59%
[29 empty] | 2020 | December | 17 | 11 | 29157.5 | 28500 | 102.3%
[29 empty] | 2020 | December | 17 | 12 | 20774 | 28500 | 72.89%
[29 empty] | 2020 | December | 17 | 13 | 10555 | 28500 | 37.04%
[29 empty] | 2020 | December | 17 | 14 | 12027.5 | 28500 | 42.2%
[29 empty] | 2020 | December | 17 | 15 | 4650 | 28500 | 16.32%
[29 empty] | 2020 | December | 17 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 17 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 17 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 17 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 17 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 17 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 17 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 17 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 18 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 18 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 18 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 18 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 18 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 18 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 18 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 18 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 18 | 8 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 18 | 9 | 447.5 | 28500 | 1.57%
[29 empty] | 2020 | December | 18 | 10 | 1492 | 28500 | 5.235%
[29 empty] | 2020 | December | 18 | 11 | 1454.5 | 28500 | 5.104%
[29 empty] | 2020 | December | 18 | 12 | 2300 | 28500 | 8.07%
[29 empty] | 2020 | December | 18 | 13 | 416.5 | 28500 | 1.461%
[29 empty] | 2020 | December | 18 | 14 | 9331.5 | 28500 | 32.74%
[29 empty] | 2020 | December | 18 | 15 | 612 | 28500 | 2.147%
[29 empty] | 2020 | December | 18 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 18 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 18 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 18 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 18 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 18 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 18 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 18 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 19 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 19 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 19 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 19 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 19 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 19 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 19 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 19 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 19 | 8 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 19 | 9 | 1413 | 28500 | 4.958%
[29 empty] | 2020 | December | 19 | 10 | 6530 | 28500 | 22.91%
[29 empty] | 2020 | December | 19 | 11 | 330.5 | 28500 | 1.16%
[29 empty] | 2020 | December | 19 | 12 | 18460.5 | 28500 | 64.77%
[29 empty] | 2020 | December | 19 | 13 | 5560.5 | 28500 | 19.51%
[29 empty] | 2020 | December | 19 | 14 | 331 | 28500 | 1.161%
[29 empty] | 2020 | December | 19 | 15 | 2831 | 28500 | 9.933%
[29 empty] | 2020 | December | 19 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 19 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 19 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 19 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 19 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 19 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 19 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 19 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 20 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 20 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 20 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 20 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 20 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 20 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 20 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 20 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 20 | 8 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 20 | 9 | 15624 | 28500 | 54.82%
[29 empty] | 2020 | December | 20 | 10 | 7886.5 | 28500 | 27.67%
[29 empty] | 2020 | December | 20 | 11 | 29196.5 | 28500 | 102.4%
[29 empty] | 2020 | December | 20 | 12 | 26835.5 | 28500 | 94.16%
[29 empty] | 2020 | December | 20 | 13 | 27427 | 28500 | 96.24%
[29 empty] | 2020 | December | 20 | 14 | 18424.5 | 28500 | 64.65%
[29 empty] | 2020 | December | 20 | 15 | 5739 | 28500 | 20.14%
[29 empty] | 2020 | December | 20 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 20 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 20 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 20 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 20 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 20 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 20 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 20 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 21 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 21 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 21 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 21 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 21 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 21 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 21 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 21 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 21 | 8 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 21 | 9 | 389 | 28500 | 1.365%
[29 empty] | 2020 | December | 21 | 10 | 1001.5 | 28500 | 3.514%
[29 empty] | 2020 | December | 21 | 11 | 14790.5 | 28500 | 51.9%
[29 empty] | 2020 | December | 21 | 12 | 7225 | 28500 | 25.35%
[29 empty] | 2020 | December | 21 | 13 | 1696.5 | 28500 | 5.953%
[29 empty] | 2020 | December | 21 | 14 | 6640.5 | 28500 | 23.3%
[29 empty] | 2020 | December | 21 | 15 | 536 | 28500 | 1.881%
[29 empty] | 2020 | December | 21 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 21 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 21 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 21 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 21 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 21 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 21 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 21 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 22 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 22 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 22 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 22 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 22 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 22 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 22 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 22 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 22 | 8 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 22 | 9 | 1379 | 28500 | 4.839%
[29 empty] | 2020 | December | 22 | 10 | 9678.5 | 28500 | 33.96%
[29 empty] | 2020 | December | 22 | 11 | 11363 | 28500 | 39.87%
[29 empty] | 2020 | December | 22 | 12 | 7653.5 | 28500 | 26.85%
[29 empty] | 2020 | December | 22 | 13 | 3864 | 28500 | 13.56%
[29 empty] | 2020 | December | 22 | 14 | 478.5 | 28500 | 1.679%
[29 empty] | 2020 | December | 22 | 15 | 95 | 28500 | 0.3333%
[29 empty] | 2020 | December | 22 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 22 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 22 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 22 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 22 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 22 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 22 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 22 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 23 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 23 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 23 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 23 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 23 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 23 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 23 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 23 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 23 | 8 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 23 | 9 | 9186 | 28500 | 32.23%
[29 empty] | 2020 | December | 23 | 10 | 2557 | 28500 | 8.972%
[29 empty] | 2020 | December | 23 | 11 | 475.5 | 28500 | 1.668%
[29 empty] | 2020 | December | 23 | 12 | 8430.5 | 28500 | 29.58%
[29 empty] | 2020 | December | 23 | 13 | 794 | 28500 | 2.786%
[29 empty] | 2020 | December | 23 | 14 | 7369 | 28500 | 25.86%
[29 empty] | 2020 | December | 23 | 15 | 7348 | 28500 | 25.78%
[29 empty] | 2020 | December | 23 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 23 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 23 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 23 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 23 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 23 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 23 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 23 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 24 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 24 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 24 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 24 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 24 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 24 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 24 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 24 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 24 | 8 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 24 | 9 | 10272.5 | 28500 | 36.04%
[29 empty] | 2020 | December | 24 | 10 | 22854.5 | 28500 | 80.19%
[29 empty] | 2020 | December | 24 | 11 | 16401 | 28500 | 57.55%
[29 empty] | 2020 | December | 24 | 12 | 12412.5 | 28500 | 43.55%
[29 empty] | 2020 | December | 24 | 13 | 3631.5 | 28500 | 12.74%
[29 empty] | 2020 | December | 24 | 14 | 3620 | 28500 | 12.7%
[29 empty] | 2020 | December | 24 | 15 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 24 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 24 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 24 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 24 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 24 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 24 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 24 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 24 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 25 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 25 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 25 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 25 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 25 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 25 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 25 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 25 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 25 | 8 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 25 | 9 | 7347 | 28500 | 25.78%
[29 empty] | 2020 | December | 25 | 10 | 4735 | 28500 | 16.61%
[29 empty] | 2020 | December | 25 | 11 | 6781 | 28500 | 23.79%
[29 empty] | 2020 | December | 25 | 12 | 30439 | 28500 | 106.8%
[29 empty] | 2020 | December | 25 | 13 | 29088.5 | 28500 | 102.1%
[29 empty] | 2020 | December | 25 | 14 | 20392 | 28500 | 71.55%
[29 empty] | 2020 | December | 25 | 15 | 5490.5 | 28500 | 19.26%
[29 empty] | 2020 | December | 25 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 25 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 25 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 25 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 25 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 25 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 25 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 25 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 26 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 26 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 26 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 26 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 26 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 26 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 26 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 26 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 26 | 8 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 26 | 9 | 1352 | 28500 | 4.744%
[29 empty] | 2020 | December | 26 | 10 | 3065 | 28500 | 10.75%
[29 empty] | 2020 | December | 26 | 11 | 2306 | 28500 | 8.091%
[29 empty] | 2020 | December | 26 | 12 | 4674 | 28500 | 16.4%
[29 empty] | 2020 | December | 26 | 13 | 1802 | 28500 | 6.323%
[29 empty] | 2020 | December | 26 | 14 | 1043.5 | 28500 | 3.661%
[29 empty] | 2020 | December | 26 | 15 | 332.5 | 28500 | 1.167%
[29 empty] | 2020 | December | 26 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 26 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 26 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 26 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 26 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 26 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 26 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 26 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 27 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 27 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 27 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 27 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 27 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 27 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 27 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 27 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 27 | 8 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 27 | 9 | 281 | 28500 | 0.986%
[29 empty] | 2020 | December | 27 | 10 | 5795 | 28500 | 20.33%
[29 empty] | 2020 | December | 27 | 11 | 30188.5 | 28500 | 105.9%
[29 empty] | 2020 | December | 27 | 12 | 21833.5 | 28500 | 76.61%
[29 empty] | 2020 | December | 27 | 13 | 19230 | 28500 | 67.47%
[29 empty] | 2020 | December | 27 | 14 | 20857.5 | 28500 | 73.18%
[29 empty] | 2020 | December | 27 | 15 | 9298 | 28500 | 32.62%
[29 empty] | 2020 | December | 27 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 27 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 27 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 27 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 27 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 27 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 27 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 27 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 28 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 28 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 28 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 28 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 28 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 28 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 28 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 28 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 28 | 8 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 28 | 9 | 1783 | 28500 | 6.256%
[29 empty] | 2020 | December | 28 | 10 | 8170.5 | 28500 | 28.67%
[29 empty] | 2020 | December | 28 | 11 | 9168 | 28500 | 32.17%
[29 empty] | 2020 | December | 28 | 12 | 20576 | 28500 | 72.2%
[29 empty] | 2020 | December | 28 | 13 | 7354 | 28500 | 25.8%
[29 empty] | 2020 | December | 28 | 14 | 5574 | 28500 | 19.56%
[29 empty] | 2020 | December | 28 | 15 | 1041 | 28500 | 3.653%
[29 empty] | 2020 | December | 28 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 28 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 28 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 28 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 28 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 28 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 28 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 28 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 29 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 29 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 29 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 29 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 29 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 29 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 29 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 29 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 29 | 8 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 29 | 9 | 738.5 | 28500 | 2.591%
[29 empty] | 2020 | December | 29 | 10 | 1303 | 28500 | 4.572%
[29 empty] | 2020 | December | 29 | 11 | 4967 | 28500 | 17.43%
[29 empty] | 2020 | December | 29 | 12 | 8152.5 | 28500 | 28.61%
[29 empty] | 2020 | December | 29 | 13 | 1474.5 | 28500 | 5.174%
[29 empty] | 2020 | December | 29 | 14 | 2503.5 | 28500 | 8.784%
[29 empty] | 2020 | December | 29 | 15 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 29 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 29 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 29 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 29 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 29 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 29 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 29 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 29 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 30 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 30 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 30 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 30 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 30 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 30 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 30 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 30 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 30 | 8 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 30 | 9 | 14558 | 28500 | 51.08%
[29 empty] | 2020 | December | 30 | 10 | 18811.5 | 28500 | 66.01%
[29 empty] | 2020 | December | 30 | 11 | 19419.5 | 28500 | 68.14%
[29 empty] | 2020 | December | 30 | 12 | 15856 | 28500 | 55.64%
[29 empty] | 2020 | December | 30 | 13 | 6775.5 | 28500 | 23.77%
[29 empty] | 2020 | December | 30 | 14 | 9759.5 | 28500 | 34.24%
[29 empty] | 2020 | December | 30 | 15 | 10637.5 | 28500 | 37.32%
[29 empty] | 2020 | December | 30 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 30 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 30 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 30 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 30 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 30 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 30 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 30 | 23 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 31 | 24 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 31 | 1 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 31 | 2 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 31 | 3 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 31 | 4 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 31 | 5 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 31 | 6 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 31 | 7 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 31 | 8 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 31 | 9 | 2418 | 28500 | 8.484%
[29 empty] | 2020 | December | 31 | 10 | 4060 | 28500 | 14.25%
[29 empty] | 2020 | December | 31 | 11 | 3968 | 28500 | 13.92%
[29 empty] | 2020 | December | 31 | 12 | 2884 | 28500 | 10.12%
[29 empty] | 2020 | December | 31 | 13 | 1223.5 | 28500 | 4.293%
[29 empty] | 2020 | December | 31 | 14 | 1186 | 28500 | 4.161%
[29 empty] | 2020 | December | 31 | 15 | 1091 | 28500 | 3.828%
[29 empty] | 2020 | December | 31 | 16 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 31 | 17 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 31 | 18 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 31 | 19 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 31 | 20 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 31 | 21 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 31 | 22 | 0 | 28500 | 0%
[29 empty] | 2020 | December | 31 | 23 | 0 | 28500 | 0%
Note on C4: Henry Metcalfe: 10-30
Note on C5: Henry Metcalfe: 70-90
Note on C6: Henry Metcalfe: 10-20

## Building Performance
XXXXX - Project Name
Building Performance Prediction
[7 empty] | Battery Charge Rate | 0
| January | July |  | Largest Battery Storage Level (kWh) |  |  |  | 0 | No | Battery? | [16 empty] | Type | Apparent Power, Occupancy Weighted (kVA)
| Predicted Demand (kWh/day) | Predicted Demand (kWh/day) | [6 empty] | No | Optimised?
| 0 | 0 |  | January
| Adjusted Demand (kWh/day) | Adjusted Demand (kWh/day) |  | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 |  |  |  |  | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 |  | Upper | Lower
| 0 | 0 | % Sun | 0% | 0% | 0% | 0.05394% | 7.896% | 14.02% | 17.75% | 19.99% | 17.88% | 14.41% | 7.963% | 0.03677% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  | Jan | January Heating & Cooling Load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Percentile | Percentile
| Renewable Savings (%) | Renewable Savings (%) | PV kW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Base Load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 80% | 30%
| #DIV/0! | #DIV/0! | Batt kW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | January Diversified Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Less Demand | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Feb | February Heating & Cooling Load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | February | [22 empty] | Base Load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 |  |  |  | February Diversified Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | % Sun | 0% | 0% | 0% | 4.577% | 9.994% | 14.25% | 15.36% | 15.44% | 14.46% | 12.15% | 9.515% | 4.232% | 0.01749% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  | Mar | March Heating & Cooling Load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| February | August | PV kW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Base Load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Predicted Demand (kWh/day) | Predicted Demand (kWh/day) | Batt kW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | March Diversified Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Less Demand | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Apr | April Heating & Cooling Load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Adjusted Demand (kWh/day) | Adjusted Demand (kWh/day) |  | March | [22 empty] | Base Load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 |  |  |  | April Diversified Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Renewable Savings (%) | Renewable Savings (%) | % Sun | 0% | 0.01201% | 2.188% | 6.717% | 10.44% | 12.19% | 13.54% | 13.12% | 13.52% | 10.88% | 9.393% | 6.118% | 1.883% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  | May | May Heating & Cooling Load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| #DIV/0! | #DIV/0! | PV kW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Base Load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Batt kW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | May Diversified Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Less Demand | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Jun | June Heating & Cooling Load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | April | [22 empty] | Base Load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| March | September |  | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 |  |  |  | June Diversified Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Predicted Demand (kWh/day) | Predicted Demand (kWh/day) | % Sun | 0.01277% | 0.7687% | 3.84% | 7.057% | 9.991% | 11.38% | 12.83% | 13.13% | 12.56% | 10.45% | 9.008% | 6.042% | 2.651% | 0.2889% | 0% | 0% | 0% | 0% | 0% | 0% |  |  | Jul | July Heating & Cooling Load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | PV kW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Base Load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Adjusted Demand (kWh/day) | Adjusted Demand (kWh/day) | Batt kW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | July Diversified Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Less Demand | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Aug | August Heating & Cooling Load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Renewable Savings (%) | Renewable Savings (%) |  | May | [22 empty] | Base Load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| #DIV/0! | #DIV/0! |  | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 |  |  |  | August Diversified Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | % Sun | 0.3906% | 1.68% | 4.817% | 7.887% | 10.56% | 11.58% | 12.41% | 11.9% | 11.31% | 9.778% | 8.231% | 5.864% | 2.85% | 0.6837% | 0.06882% | 0% | 0% | 0% | 0% | 0% |  |  | Sep | September Heating & Cooling Load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | PV kW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Base Load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Batt kW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | September Diversified Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| April | October | Less Demand | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Oct | October Heating & Cooling Load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Predicted Demand (kWh/day) | Predicted Demand (kWh/day) |  | June | [22 empty] | Base Load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 |  |  |  | October Diversified Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Adjusted Demand (kWh/day) | Adjusted Demand (kWh/day) | % Sun | 0.693% | 1.878% | 4.945% | 8.011% | 9.978% | 11.14% | 11.31% | 11.56% | 11.28% | 9.643% | 8.565% | 6.028% | 3.456% | 1.121% | 0.3835% | 0% | 0% | 0% | 0% | 0% |  |  | Nov | November Heating & Cooling Load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | PV kW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Base Load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Renewable Savings (%) | Renewable Savings (%) | Batt kW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | November Diversified Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| #DIV/0! | #DIV/0! | Less Demand | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Dec | December Heating & Cooling Load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | July | [22 empty] | Base Load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 |  |  |  | December Diversified Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | % Sun | 0.4615% | 1.537% | 4.455% | 7.481% | 10.13% | 10.8% | 11.42% | 11.85% | 10.8% | 10.72% | 8.698% | 6.504% | 3.659% | 1.214% | 0.2777% | 0% | 0% | 0% | 0% | 0%
| May | November | PV kW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Predicted Demand (kWh/day) | Predicted Demand (kWh/day) | Batt kW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Less Demand | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Adjusted Demand (kWh/day) | Adjusted Demand (kWh/day) |  | August
| 0 | 0 |  | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00
| Renewable Savings (%) | Renewable Savings (%) | % Sun | 0.07592% | 1.041% | 3.998% | 7.397% | 9.762% | 10.92% | 12.78% | 13.01% | 11.4% | 10.92% | 8.807% | 6.161% | 3.083% | 0.6241% | 0.01739% | 0% | 0% | 0% | 0% | 0%
| #DIV/0! | #DIV/0! | PV kW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Batt kW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Less Demand | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September
| June | December |  | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00
| Predicted Demand (kWh/day) | Predicted Demand (kWh/day) | % Sun | 0% | 0.3582% | 3.548% | 7.972% | 10.62% | 13.18% | 13.05% | 12.35% | 12.96% | 10.45% | 8.729% | 5.198% | 1.563% | 0.02496% | 0% | 0% | 0% | 0% | 0% | 0%
| 0 | 0 | PV kW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Adjusted Demand (kWh/day) | Adjusted Demand (kWh/day) | Batt kW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Less Demand | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Renewable Savings (%) | Renewable Savings (%) |  | October
| #DIV/0! | #DIV/0! |  | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00
|  |  | % Sun | 0% | 0% | 2.278% | 8.291% | 12.53% | 14.72% | 13.63% | 14.62% | 13.6% | 10.05% | 8.013% | 2.236% | 0.03176% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | PV kW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Batt kW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Less Demand | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November
|  |  |  | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00
|  |  | % Sun | 0% | 0% | 0% | 3.783% | 10.53% | 17.82% | 18.42% | 17.4% | 14.62% | 11.37% | 6.066% | 0.00264% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | PV kW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Batt kW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Less Demand | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December
|  |  |  | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00
|  |  | % Sun | 0% | 0% | 0% | 0.0407% | 8.903% | 15.28% | 21.4% | 22.27% | 15.74% | 11.56% | 4.812% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | PV kW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Batt kW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Less Demand | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
© Henry Metcalfe, 2024